    Lemoine Family Builders, Inc.

                                       2205 Roosevelt Blvd.




    Kenner, LA   70062
                  Office: 504-739-9992     Fax: 504-305-0197

                                    lembuilder@aol.com
                              Louisiana State License #34483

REQUEST FOR INFORMATION

Project: Marco's Pizza

2349 E. Gause Blvd.

Slidell, LA

Date:

November 8, 2010




From:
Cal Lemoine


Attn:

Robert Wiltse 






Project Manger

Company:
Dammon Engineering, Inc.

Phone:

985-649-5832


Fax:

985-641-5950

_______________________________________________________________________________

Mr. Wiltse,

The following is a list of items that were discussed at a site meeting of Marco's Pizza, 2349 E. Gause Blvd, Slidell on November 08, 2010.

· Will the building permit by supplied by the Owner/Architect or Builder?

The builder will be responsible for obtaining the permit.  The city of Slidell does not have an IBC plans review section, so the owner has obtained the plans review from a third party.  The fees for the permit will be the builder’s responsibility.

· Please verify what items will be supplied by Landlord or Owners, (i.e. equipment, cooler, case work, signage, etc)  All items on the equipment list A-2 and signage will be provided by Owner.
· Wall Art & Wall Mural's, who supplies / installs these items?  Art & Mural’s by Owner.
· Electrical:

1. E-1 - "Electrical Notes" #12, reference to using NMC cable to lights, receptacle circuits.  E-2 - "Raceway Systems" note "A", reference to using EMT or Electrical Metal Tubing. Please verify.  E-1 Note #12 has been revised to remove the use of NMC cable for lights, receptacle circuits.
Other revision to the electrical documents is for the Conveyor Oven breaker to be shunt-trip.

· HVAC: (Please verify that the following equipment will be supplied by owners)

1. Bathroom fan and duct (to be reused).  The existing equipment to be reused.
2. Refrigeration equipment  All items on the equipment list A-2 will be provided by Owner however the new HVAC will be the responsibility of the contractor.
3. Walk-in cooler and assembly.  All items on the equipment list A-2 will be provided by Owner however the new HVAC will be the responsibility of the contractor.
4. Hood, hood fans, fan curbs and controls.  All items on the equipment list A-2 will be provided by Owner, except the ANSUL system will be provided by contractor.
· Plumbing:

1. P-1 - "Plumbing Fixture Schedule" calls for 200 gallon Grease Trap. Plans indicate existing 60 gallon grease trap. Plans do not show second grease trap. Will a 200 gallon grease trap be added?  The existing 60-gallon grease trap is to be used; the plans have been revised to reflect this.

2. P-1 - "Plumbing Key Notes" #09, calls for 1" gas line to 80 gallon water heater.  Plan notes to refurbish existing water heater, that is a 50 gallon electric water heater. Please advise which is correct.  Plumbing Key Note #9 does not apply, all Plumbing Key Notes have been removed from the drawing.  The existing 50-gallon electric water heater is to be reused.
· Framing:

1. Elevation of solid blocking?  This is a new franchise and we do not have elevations.
2. Plans note that the demising partition is "Existing 2hr rated wall". This wall is a 1hr rated wall. Please advise.  According to the landlord this is an existing 2-hour rated wall and he had this building built.  I could not verify that each side of the wall has two layers during the site visit.  If the existing wall is a 1-hour rating, then I will write a letter to the Fire Marshal and the city explaining that a 1-hour rating is sufficient for this installation.
Sincerely,

Cal Lemoine 

Lemoine Family Builders, Inc.

PAGE  
2

