    Lemoine Family Builders, Inc.

                                       2205 Roosevelt Blvd.




    Kenner, LA   70062
                  Office: 504-739-9992     Fax: 504-305-0197

                                    lembuilder@aol.com
                              Louisiana State License #34483

REQUEST FOR INFORMATION

Project: Marco's Pizza

532  Gause Blvd.

Slidell, LA

Date:

November 22, 2010




From:
Cal Lemoine


Attn:

Robert Wiltse 






Project Manger

Company:
Dammon Engineering, Inc.

Phone:

985-649-5832


Fax:

985-641-5950

_______________________________________________________________________________

Mr. Wiltse,

The following is a list of items that were discussed at a site meeting of Marco's Pizza, 532 Gause Blvd, Slidell on November 19, 2010.

· Is replacement of broken storefront glass on Gause Blvd. side of suit be included in our scope?  Take first two windows out and install panel insert.
·  Wall details AA & AB, method of screening backside of partition assembly from exterior of glass storefront?  Blackout paint shall be applied up to where the window meets the top ledge of the mid-height wall.
· Plumbing:

1. Will existing water meter be reused?  Use the existing water meter.

2. "Rear exterior wall", please verify that all waste water lines be installed above the slab and a step will be constructed to conceal all waste lines. (as per Bobby Curtis)  This is correct, see detail.
3. Location and size of water heater?  The location of the water heater is above the mop sink and the size is listed in the General Notes F. as a 50-gallon with quick recovery.  See attached detail.

4. Will existing restroom fixtures be replaced?  Replace the water closet and relocate existing hand sink.
5. Will plumbing be needed for a icemaker?  No
6. Will plumbing be needed for a beverage station?  No
7. Dumpster Pad:


a. Grease trap location between dumpster and sanitary sewer?  Bobby is going to contact Bears next door about sharing their grease trap for their dumpster.  Otherwise, install a small grease trap between the dumpster drain and the existing sanitary sewer line (the existing sewer line is on the building opposite from the dumpster pad).


b. Water source, is a second meter added for the dumpster pad, or is water piped  


from Marco's Pizza suit?  The landlord has not identified a second source of water for the dumpster pad.  Hot and Cold water is required near the dumpster site.  Install either both hot and cold water from the store or cold water only from the store and a tank-less water at the site depending on costs.  


c. Hot water, is a tank less water heated added at the dumpster location, or is hot 


water piped from the Marco's Pizza suite?  See above.

Sincerely,

Cal Lemoine 

Lemoine Family Builders, Inc.

PAGE  
1

