Dammon Engineering, Inc.

dammonengineering.com


554 Old Spanish Tr.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

June 6, 2011
Mr. Patrick Flory
Office of State Fire Marshal

New Orleans District

8181 Independence Blvd.

Baton Rouge, LA 70806

RE:  
P0399333

Marco’s Pizza
4638 LA Hwy 22
Mandeville, LA  70448
Dear Mr. Flory,

With regard to the above referenced project:
Item #7, 101:8.2.3  Fire resistive-rated building assemblies shall be of a design that has been tested and listed by an approved testing laboratory for the intended application. (NFPA 251:1-3.2 does not permit variations from test assemblies).  (2-HOUR DEMISING WALL DOES NOT HAVE A LISTING.)

Item 7 Response: On drawing A-1 replace 2-hour rated assembly GA File No. WP1521 used for the demising wall, with UL Design No. U419 2-hour rating, see attached.

Item #19, RS 23:536  Boilers, Pressure Vessels, and water heaters of 50 gallon capacity or larger and/or 100,000 BTU/HR heat input shall conform with the provisions of the Louisiana Boiler Inspection Law in accordance with adopted rules and regulations.  (Contact our Boiler Section ( 800-256-5452 ) with any questions concerning this requirement.) 

Item #19 Response:  On drawing P-1, Plumbing Fixture Schedule, replace the description for the hot water heater:   A.O. SMITH BT-80 W/ DRAFT DIVERTER to 50 GALLON ELECTRIC HOT WATER HEATER.

If you have any questions, please feel free to call.

Sincerely,

Robert Wiltse
Chief Architect

