                                                                                                                                 8-17-05

St. Tammany Parish

Plumbing Inspector

Dear Mr. Reiling,


Please be advised that the P-1 drawing for Northshore Daiquiris To-Go has been revised to read:

Plumbing note #16 which currently reads:

16. Hot water heater pressure relief must be connected indirectly to the sanitary sewer system or directly to the outside. Hot water capacity shall be no less than 50 gal.

Shall be revised to state that:

16. Water heater pressure relief valve outlet and safety pan drain shall be directly piped to outside of the building so that any discharge can cause no personal injury or property damage and can be readily observed by the building occupants. Relief valve and safety pan drain piping shall contain no valves or traps and shall be so graded and connected as to drip to the discharge end of the piping by gravity. Discharge piping shall terminate no less than 6” and no greater than 24” above finish grade.

Thank you,

David Dammon

Project Manager

Dammon Engineering

(985) 649-5832

