Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

8-17-2005

St. Tammany Parish

Plumbing Inspector

Mr. Larry Reiling

RE:  Northshore Daiquiris To-Go

       Renee Cannizzaro

       1102 Hwy. 190

       Covington, La

Dear Mr. Reiling,


Please be advised that the P-1 drawing for referenced site has been revised:

Plumbing note #16 currently reads:

16. Hot water heater pressure relief must be connected indirectly to the sanitary sewer system or directly to the outside. Hot water capacity shall be no less than 50 gal.

Revised to state:

16. Water heater pressure relief valve outlet and safety pan drain shall be directly piped to outside of the building so that any discharge can cause no personal injury or property damage and can be readily observed by the building occupants. Relief valve and safety pan drain piping shall contain no valves or traps and shall be so graded and connected as to drip to the discharge end of the piping by gravity. Discharge piping shall terminate no less than 6” and no greater than 24” above finish grade.

Thank you,

David Dammon

Project Manager

Dammon Engineering

(985) 649-5832

