January 15, 2009

Mr. W. Ray Treadaway, Jr.

I. C. C.  Certified Building Plans Examiner

Diversified Building Services, Inc.

Re:
Plumbers’ & Steamfitters’ Local 60

427 Ozone Park Road

Covington, Louisiana

Dear Mr. Treadaway,

I am writing this letter to you today in response to the Plan Review that your firm submitted to the City of Covington regarding the above referenced project.  Please accept the following explanations for items as outlined in your Plan Review letter dated 27 December 2008.

Page 1, Item No. 3:

The new facility only affects approximately 425 square feet of the 19,200 square foot site.  This improvement is being built where an existing foundation is located and does not create any new drainage impact and it’s less than 50% of the overall site improvements.  We will, however, be providing downspouts that will drain into the existing sheet flow drainage of the site that is currently in place.

Page 2, Item No. 4: 

All existing landscaping shall remain the same.  This improvement is less than 50% of the overall site and does not require landscaping improvements.

Page 3, Item No. 7:
There is no new outdoor lighting required for this project.

Page 4, Item No. 8:

The building will be utilized by the existing occupant load; therefore no additional parking area is required other than what currently exists.

Page 5, Mechanical & Plumbing:

This is a facility that is being used to demonstrate plumbing and mechanical installations.  These installations will only be temporary by nature and will not be for public use.  There is no sewer or water connections provided for this project due to the fact that plumbing will only be design and concept.

If you have any questions, or require any additional information, please feel free to call.

Sincerely,

Chuck Dammon

Dammmon Engineering, Inc.

