INTERNATIONAL BUILDING CODE 2006 REQUIREMENTS

# CDCAI / NEW OFFICE BUILDING
JOB #2030

Occupancy Classification:
Business, Group B. (Sect. 304.1)
Assembly, Group A-3. (Sect. 303.1)

Occupant Load: (TBL 1004.1.1)
Business Areas = 100 Gross sq. ft. / occupant
Assembly Areas = 1004.7 Fixed Seating, number of seats, 294.
5,189 s.f. Business = 52 occupants
9,900 s.f. Gross Building
Total of 346 occupants

Exit Access Requirements: (Sect. 1015)
2 exits required for > 49 occupants in business occupancy. (2 exits provided).
2 exits required for > 49 occupants in assembly occupancy, (2 exits provided).

Exit Access Travel Distance: (Sect. 1016)
Exit access travel distance = 200’ unsprinkled.

Allowable Height and Bldg. Area: (TBL 503)
B = 23,000 s.f. / 4 story allowed, this project 1 story 5,189 s.f.
A-3 = 9,500s.f. / 2 story allowed, this project 1 story 4,711 s.f.

Construction Classification: (Sec 602.2)
Type IIB

Fire Resistance Rating Requirements for Building Elements: (TBL 601)
Structural Frame = 0 hrs.
Bearing Walls (interior and exterior) = 0 hrs.
Non-Bearing Walls = 0 hrs.
Floor Construction = 0 hrs.
Roof Construction = 0 hrs.

Fire Resistance Rating Requirements for Exterior Walls: (TBL 602)
Exterior Walls with 10</=X<30 Fire Separation Distance = 0 hr.

Fire Alarm System Requirements: (Sec 907)
This Bldg. does not requires a Fire Alarm System in accordance with Section 907.2.1 and Section 907.2.2.

Fire Protection System Requirements: (Sec 903)
This Bldg does not require a Fire Protection System in accordance with Section 903.2.1.3 Group A-3.

Construction Documents: (Sec 1603)
This Bldg. shall be designed in accordance with IBC Section 1609 as a fully enclosed Bldg. using the following information:
Basic Wind Speed (3 second gusts) = 110 mph (Fig 1609)
Importance Factor: Category III Bldg., IE = 1.00, IS = 1.0, IW = 1.00 (TBL 1604.5)
Exposure B, determination of wind loads shall be in accordance with IBC Sec 1609.4
Minimum live loads shall be determined in accordance with TBL 1607.1
Ground snow loads = 5 psf (Fig. 1608.2)
Based on the survey of this property by Morgan Goudeau & Assoc., Registered Land Surveyor Robert Wolfe, Jr. No. 4548.
F.I.R.M. Community Map No. 220165 0175 B; Date 5-3-1982.
Flood Zone: C.