SECTION 16007

NAMEPLATES AND TAGS
1
Nameplates

1.01
Specifications


General nameplates shall be composed of laminated, phenolic plastic with bevelled edges and a white face with a black core, 1/16 inch minimum thickness, with lettering engraved through the outer covering to render black letters on a white background.  Nameplates expressing emergency conditions or instructions shall have a red face with a white core, and lettering shall be engraved to render white letters on a red background.  Lettering shall be block style, 1/8 inch minimum height, unless otherwise indicated.  Nameplates shall be permanently fastened to equipment with appropriate screws, bolts, or adhesive.  The adhesive materials shall be suitable for the surface to which the nameplate is adhered and for the type environmental conditions to which the nameplate will be exposed.

1.02
Equipment Identified


A.
Cabinets and Panels


Nameplates shall be provided to identify all equipment cabinets and panels.  Devices, including terminal blocks, inside cabinets and panels shall be identified with similar nameplates.  Identification designations shall be as indicated on the project drawings.


B.
Switches, Starters, and Receptacles



Switches, starters, and receptacles shall be identified with engraved phenolic nameplates.  The circuit number, voltage, and panel of origin shall be identified on the nameplate.
END OF SECTION


Section 16007 Page 1 of 1

