
Section 16014
SAFETY SWITCHES  -  DISCONNECT SWITCHESPRIVATE 

1.
GENERAL

1.01  The disconnect switches shall be heavy duty fusible type with a visible double break rotary blade mechanism and over-current protection through field installed fuses.

2.
RATINGS  

2.01
 240VAC, 1200 amperes, 3 pole

2.02 Switches are 100% load break and 100% load make rated.

2.03  Visible double break rotary blade mechanism. 

2.03 Two points of contact provide a positive open and close, easier operation, and also help prevent contact burning for longer contact life. 

2.05  Padlocking capability. 

2.06 Interlocking mechanism. Door cannot be opened when the handle is in the ON position. Built-in defeater mechanism provides for user access when necessary. 

2.07  Clear line shield with probe holes. 

2.08  Clearly visible palm fitting red handle. 

2.09  NEMA 3R rain-tight. 

2.10  Solid neutral (When needed)

2.11  Ground Bar

2.12  UL listed for use as service entrance

3.
FUSES

3.01 The fuses shall be 600VAC, 1000A dual element time delay Class L, with an interrupting rating of 300,000 AIC.  The fuses shall be provided and installed by the electrical contractor and of the same manufacturer.  The contractor shall provide (1) one set of spare fuses.

4.
RECOMMENDED MANUFACTURERS

4.01 The listing of specific manufacturers below does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed below are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days 

prior to bid date.  Acceptable manufactures are: 
Cutler-Hammer, Square D, General Electric

END OF SECTION
SECTION 16014    Page 1 of 2

