SECTION 16018

SWITCHBOARD

1
General

The switchboard shall be rated 1000A, 120/208 VAC, three phase, four wire, 42KA bracing, fully rated, with one front accessible vertical section containing the feeder breakers, metering and incoming main lugs.  The bus shall be copper, and the breakers shall be the bolt-on type.  The spaces shall be complete with bus and mounting provisions necessary for future expansion.

2
Metering

Provide a Veris Industries H8163-1600-4-3 containing a digital display and H8126-CV N2 communications card.  The metering unit shall include a network communications port in order to transmit all metering parameters from its network over the Customer’s existing Johnson Control Integrator network.  Contact and furnish services of Johnson Controls to furnish materials, install required apparatus and make connections to network communications port of metering unit.
3
Distribution Section


A.

Main bus shall be rated 1000 amperes. All bus bars shall be silver-plated copper with bolted connections at joints. The bus bars shall be of sufficient size to limit the temperature rise to 65 degrees C and rated to withstand mechanical forces exerted when a short-circuit current of 50,000 amperes symmetrical flows through them. Provide full capacity neutral. 

B.

The distribution section shall contain molded case circuit breakers arranged in group-mounted construction. The quantities and frame/trip sizes shall be as scheduled on the drawings. 




C.

Circuit breakers shall be operated by a toggle-type handle and shall have a quick-make, quick-break over-center switching mechanism that is mechanically trip free. Automatic tripping of the breaker shall be clearly indicated by handle position. Contacts shall be non-welding silver alloy, and arc extinction shall be accomplished by means of DE-ION arc chutes. A push-to-trip button on the front of the circuit breaker shall provide a local means of manually exercising the trip mechanism.  


D.


Circuit breakers shall have a minimum symmetrical interrupting capacity of 42KA or as indicated on the drawings.  Series rated breakers not allowed.


E.

Circuit breakers shall have thermal-magnetic trip units and inverse time-current characteristics.



F.

Operating handles shall face the front of the unitized equipment and the complete group mounted assembly shall be front accessible for installation and maintenance of outgoing cables. Conduit space shall be provided for cables exiting the top or the bottom of the section. Outgoing cable shall be confined to front accessible gutters where they do not interfere with the free flow of cooling air


G.

All circuit breakers shall be pad lockable in the open position.
4
Enclosure


The enclosure shall be a manufacturer's standard switchgear enclosure meeting all applicable standards.  The panel enclosure shall be NEMA Type 1 indoor free standing front accessible only.  


Maximum Dimensions shall be as follows:



Distribution Section 36" Wide X 30" Deep X 90" High

5
Nameplates 


A.
All compartments and devices furnished within the switchboard shall be provided with a nameplate.  All nameplates shall be two ply laminated engraved phenolic with black letters on a white background with beveled edges.


B.
Breaker's inscriptions shall include the equipment name shown on one-line diagram.


C.
All nameplates shall be attached to metal surfaces with screws or rivets only.  Self-sticking or glued nameplates will not be accepted.


D.
Nameplate sizes shall be 1” high by 3”  long, with 1/8”  high characters.

6
Testing


A.
The Contractor shall submit six copies of factory test data for acceptance before shipping of the switchgear equipment.  The factory tests shall be in accordance with the recommendation of IEEE and ANSI


B.
The switchboard unit shall be fully assembled and tested prior to shipment.  Tests on the switchboard and breakers shall include but are not limited to a contact resistance test, insulation test, breaker over current-relay trip device test and calibration and communication of networked devices.  Testing will be conducted under provisions of Section 16041.


C.
After the factory tests have been completed, the switchgear shall be disassembled into any required shipping sections with care to minimize the reassembling, connection, functional check out time in the field.


D.
The vendor as part of the contract shall provide technical assistance during the installation, checkout and start-up of the substation.  The vendor shall provide a fully qualified, factory trained manufacturer's representative and all necessary equipment and instrumentation to test, calibrate, set and functionally checkout the entire substation.  A minimum of one day of field service is required.


E. 
Recommended Manufacturer


The 120/208 VAC circuit breaker switchboard shall be Cutler-Hammer Pow-R-Line C Type 1, Square D type QED Power Style, G.E., or equal.

END OF SECTION
Section 16018 Page 1 of 3 


