HPC Switchgear Replacement

5/19/05 Submittal by Dammon & Assoc

Project # SP-2519A

6/13/05 comments by C R Troxler 

includes comments from Gus Cantrell

ELECTRICAL

SPECIFICATIONS

1. 01000

UNO will prepare the final section 01000.  You do not need to make further submittals of this section.

2. 02072
Section 2.03 should read as follows:

1. The contractor shall take ownership of all removed equipment and materials, including the transformer, switchgear, and distribution panelboard.  The contractor shall legally dispose of these and all removed/demolished materials off University property

3. 03300

Paragraph 2.04.B – specify 4000# concrete

4. 16017

Section 2.02 

Specify the values for primary voltage, configuration and BIL

Section 2.03

Specify the values for secondary voltage, configuration, and BIL.

DRAWINGS

5. S-1

Screw piles must be 6 ton.

END OF COMMENTS

