January 18, 2000

TO:
Ed Boesch


A.B.C. Electric


1846 Front Street

 
Slidell, LA  70458

RE;
La Quinta Inn; Downtown New Orleans

Dear Ed;

  I went over the electrical drawings for the project, and found that the feeder supplying MCCA (when I saw the drawings this morning MCCA had been changed to a panelboard) has to be installed using the “tap rule” for feeders.  This limits the feeder to a total of 10 ft in length, and should be noted on the drawing.  It is also questionable to have the six (6) branch feeders tapped to the one main feeder from MCC.

  I wrote to the city that we would install a 200 AMP fusible switch at that location, and that the branch circuit falls under the 10-ft tap rule.

  I had to sign the statement that I would inspect the job during construction.  The contractor can let me know what he would like to do on that part.

  I am enclosing an invoice to cover my work, stamping the drawings and the trip to New Orleans.

  I appreciate your using me in this matter.  I understand you will forward this invoice for payment.







Sincerely,







Emmett G (Pete) Dammon P.E.,

plc/EGD

