TO:
C.H. Palm 


Mathis Group

DWG E-1

1. Top of Sheet

a. Add note to feeder between MCC & MCCA (Maximum 10 ft length)

b. Encircle all feeders of MCCA and draw line to New Hex Symbol for keynote. 5

c. Add keynote #5 (Refer to Motor control center schedule for Branch circuit sizes).

2. Remove Texas (Mr. Long) stamp.

3. Remove multatech from block and add Dammon Engineering, Inc.

4. Remove stamp information at bottom and add New Orleans information and my name Emmett G. (Pete) Dammon P.E., LA #8796.

5. Remove checked by (Long) and add my name.

6. Add note to MCCA 3 pole main disconnect sw, rated 200A, fuses shall be ITT C5200 or equal (200 000 A.I.C.).

DWG E-2

1. Refer to note that reads “New Motor control center mounted on wall”.

Add to Note


(Meet Requirements of 10’ TAP rule).

Repeat (2) (3) (4) (5) above, on E-2 & E-3

