DESIGN SPECIFICATION FOR 50 HP GAS FIRED STEAM BOILER
Skid Mounted System

1.0    GENERAL

1.1 GENERAL REQUIREMENTS

Provide a 50 hp vertical tubeless steam boiler with feed water and blow-down systems with single point electrical and water connections completely pre-piped and skid mounted.  Boiler shall meet ASME Section I or Section IV.  The packaged system to supply steam using softened city water from the boiler house water treatment system.

1.2 WORK INCLUDED

Furnish and install a complete packaged vertical two pass steam boiler system with all accessories skid mounted, wired and piped at the manufacture of the boiler facility as indicated on the drawings and as specified herein.

1.3 RELATED WORK SPECIFIED ELSEWHERE

N/A

2.0 PRODUCTS

2.1
MANUFACTURERS
A.  Fulton Boiler Works
B.  Miura Boiler, Inc.

2.2
STEAM BOILERS

A.  General
The contractor shall furnish a 50 hp natural gas fired steam boiler with modulating firing rate.  The steam boiler shall be of the vertical type and shall be constructed in accordance with the ASME section I or section IV, 150 psig MAWP.  Boiler unit shall consist of a vertical tubeless boiler, boiler fittings, burner equipment, and automatic controls.  The boiler (with all piping and wiring) shall be factory assembled as a self contained unit.  Boiler shall be neatly finished, thoroughly tested, and properly packaged for shipment.  Both boiler and burner must be the product of the same manufacturer to assure undivided responsibility and simplified servicing.  The boiler shall be inspected, certified, and bear all applicable national and local code labels.  Boiler trim shall include relief valves dial type pressure gauge, low water cut off, and other items as required.  The complete boiler shall carry the Underwriters Laboratory (UL) Label.
B.  Capacity

The boiler shall have a capacity of 1,725 lbs/hr steam, with output of 1,674,000 but/hr @ natural gas use of 2,100 (CFH) mbtu

C.  Refractory Material

All refractory material shall consist of non-asbestos materials. The boiler section subject to direct flame shall be insulated with a high strength, low permanent linear change, high temperature limit castable material for vertical tubeless boilers. Ceramic fiber insulation can be used for Vertical Multiport Boilers.

D.  Access
An observation port shall be provided to view the combustion chamber.  Unit shall be of gas-tight construction throughout.  Handholes and cleanout openings shall be provided at the lower part of boiler so that the entire bottom of the boiler may be cleaned.

E.  Boiler Trim

Boiler trim shall include safety relief valve(s), complete probe type level control system to include feed pump, on/off control, and redundant low water cutoff.  In addition, dial-type press gauge and stack temperature gauge shall be incorporated.  Feedwater stop and check valves with fast closure and slow-opening blowdown valves incorporated as part of the complete package.  Water column blowdown valve and steam stop valve shall be provided.

F.  Vessel

Pressure vessel shall contain no tubes.  Unit shall be provided with lifting hooks and a 14 gauge stainless steel jacket, and high temperature blanket insulation.
G.  Factory Assembly

Units shall be assembled and wired with burner controls and trim.

H.  Fuel Burning Equipment

Fuel-burning equipment shall be forced draft type-assembled wired, mounted, and tested at the factory.  The entire unit shall be ready for field connection to power and fuel supply.  equipment shall include forced draft fan, flame sensing device, and control cabinet containing electronic flame safeguard and programmer and indicating lights for major operations.  Low Emissions (LE) burners are required, the burning equipment shall produce stack emissions of less than 30 ppm with oxygen corrected to 3%.  Combustion air shall be preheated by flue gas.

I.  Motors and Controls

All motors shall be suitable for 208 volt, 60 hertz, three phase operation.  Controls shall be 115 volt, 60 hertz, single phase.  Magnetic motor starters or motor contactors, depending on voltage, shall be provided in the control cabinet.
J.  Gas Burner

Gas burner shall be vertically oriented, top mounted, downfired forced draft type with the following features:  a main gas control group consisting of an automatic gas valve, automatic safety gas valve, gas volume modulating control valve, gas pressure regulator, gas cock, gas pressure gauge, and gas-electric ignition assembly consistent of a pilot burner 6,000 volt ignition transformer, flame rod or UV scanner, air flow safety switch.  Gas fired boilers over 30 hp shall have modulated burners.  LE burners for boilers 40 hp and larger shall use a Siemans linageless modulation gas train.

K.  Controls

Operating pressure control for automatic start and stop of burner operation.
Two low water cut-off probes to cause shut down of unit  when water level drops to minimum safe level, (one in the water column and on in the boiler shell).  The one in the shell shall be manual reset to comply with ANSI/ASME CSD-1 Code
Boiler shall have an air safety switch to prevent operation until sufficient combustion air is assured. 
A contact for the feedwater pump shall be included and consist of a single phase pump motor starter or contacts for 3 phase pump. 
The control shall maintain a running history of operating hours, number of cycles, and the most recent six flame failures.  This control shall have the capability to be connected to a keyboard display module which will retrieve that information.  
Burner motor controller shall have thermal overload protecttion.  
All controls to be panel mounted and so located on the boiler to provide ease of servicing the burner and boiler without disturbing the controls; and also located to prevent possible damage by water, fuel or heat of combustion gases.  Controls connected to water or fuel shall be installed outside the main boiler control panel. 
All controls shall be mounted and wired according to Underwriters’ Laboratories requirements.
This unit will be the lead boiler, connected to an existing boiler located in the same boiler.  The package shall include a lead lag system capable of sequencing the boilers and changing the lead boiler designation automatically.-
L.  Contractors shall immediately report any asbestos found on pipe, etc. in his area of work to the hospital maintenance, supervisor, and discontinue work in that area until cleared to continue by Maintenance supervisor.
2.3     SUBMITTALS
A.  Submit three copies of

                        1.  Boiler and skid package
                        2.  Pumps and motors and associated equipment mounted on

                             skid.

                        3.  All valves, fittings, pipe and pipe hangars.

                        4.  Insulation.

                        5.  Flue and roof patching materials.  

                        6.  Controls.

                        7.  Shop drawings as listed in 3.3 below.

2.4     CONDENSATE RETURN/FEEDWATER SYSTEM

The condensate return/feedwater system shall be a horizontally of vertically oriented vented system complete with a water level gauge glass, mechanical float type makeup water valve assembly and (2) pump(s).  This system will be factory assembled and tested, including leak test to insure proper manufacturing. The system shall have a primer coat and finish coat of paint.  Feedwater pumps shall providefeedwater and flow at a rate of 2.5 times the boiler evaporation rate for 105% of boiler pressure.  Low pressure boilers (<30psi) shall have feedwater pump flow control valves.  Stainless steel pump internals shall be used.

2.5     BLOW-OFF SEPARATOR

The boiler blow-off separator shall be ASME Section VIII Div. I approved and National Board registered pressure vessel.  The unit shall carry the “U” stamp and be rated for 75 psi in accordance with the 1991 National Boiler Blow-off Code.  The separator shall be constructed of a minimum of 3/8” thick steel shell and 5/8” thick flatheads.  Vessel shall have a centrifugally baffled blow-off inlet to allow for the flashing of steam.  It shall have adequate handhole openings to allow for internal inspection of vessel.  The connections to be included on this vessel are a top vent for steam flash release, a bottom drain, a blowoff inlet and outlet as well as a cold water inlet.  The system shall include an automatic cooling kit to insure that the proper blow-off water temperature is maintained before draining to the sewer system.  The blow-off separator shall have a primer and finish coat of paint.

2.51   BOILER SOLIDS MANAGEMENT

Provide an automatic blow-down valve with timer for fully automatic control of bottom boiler blow-off.  This used in conjunction with the conductivity-based automatic surface blowdown will allow totally unmanned operation of blow-off which is essential to boiler pressure vessel longevity
2.6     SKID MOUNTING

All the components in this specification shall be mounted on a steel skid with the appropriate number of lifting holes to insure ease of movement and installation of system.  The steel skid shall be constructed of ¼” thick steel decking material welded to 4” structural steel channel primed and painted.  All components shall be welded, except that boiler shall be bolted (use accessible nuts and bolts) to the deck of the skid to insure that no movement is possible in shipment. (Boiler must be disconnected from skid in order to transport the boiler through  main door of boiler house)  All components are to be completely piped and wired. Two check valves shall be included on the feedwater line to the boiler. All blow-down pipe fittings are to be forged steel.  All interconnecting steel piping shall be schedule 80.

2.61   SINGLE SOURCE POWER CONNECTION

Single source power connection shall allows for a single power connection to the skid system that will then control all the components on the skid.  This will include a fused disconnect NEMA 4 STAINLESS STEEL water tight as well as a control circuit transformer (3 phase).  It shall also include all wiring to both 3 phase and single phase requirements.

2.62   SINGLE POINT WATER AND STEAM CONNECTIONS
All cold water piping to the blow-off separator and return system shall be on a common header to allow a single water connection.  The piping from the steam outlet to the return system preheat kit shall be included.
3.0     EXECUTION

3.1     FACTORY TESTING

A.  Boiler inspection shall include a hydrostatic test in the presence of an inspector having a National Board Commission.  He shall certify a Data Report which shall be delivered with the boiler as evidence of ASME Code compliance.  In addition to an ASME
symbol, the boiler shall bear a National Board Registration Number.

B.  Proper operation of the boiler and all controls will be assured by filling with water and test firing at the factory.  Test firing will include adjusting all operating and safety controls to the correct settings.

C.  Hydrostatic test of boiler external piping shall be included with skid-mounted systems.  

3.2     START-UP AND WARRANTY SERVICE

A.  The boiler installation shall be inspected by the manufacturer prior to start-up.

B.  The field start-up of the boiler shall be performed by factory certified mechanics.

C.  The pressure vessel shall have a 10 year (120 month) material and workmanship warranty, when furnished as part of the pre-piped system.  All other components shall be covered by a one year (12month) warranty.
D.  Instructions for installation I, operation, and maintenance of the boiler and a wiring diagram, shall be contained in a manual provided with boiler unit (Three copies).
E.  Wiring diagram specific to the boiler, shall be included in the boiler  panel box.

3.3     SHOP DRAWINGS
A. Submit three (3) copies
B. Shop drawing submittal data shall clearly and concisely address all specification requirements listed herein, certification data and shop drawings requirements.
C. Shop drawings shall indicate construction materials of boiler.  The submittal shall include wiring diagrams, piping diagrams, and detailed dimensional data which shall be specific to the project.   Standard piping, wiring, control diagrams and other submittal data that are not specific to this project will not be acceptable.  Shop drawings shall depict location of unions etc. that must be used to disconnect or connect the boiler to the skid and skid mounted items and to the water blowdown and natural gas piping, when removing and reinstalling boiler on the skid shop drawings requirements.
1

