Each side was successfully tested at 30 psi.
The combination of this type material for the sides, ends and roof of your unit, all connected together as a unibody and connected then to the steel frame with metal ties, along with doors and windows that are rated at least 8 psi by their builder will provide excellent blast protection for personnel in the structure.

Dammon Engineering did not design the air conditioning, plumbing and electrical systems for the building and we have no knowledge of these systems and the possible consequences to the systems by a blast, but the following should be considered:

1.  The air conditioning system should include an outside air source that complies with present day standards for fresh air.  In case of a blast, this must be automatically closed off and remain so until mechanically opened after it is determined safe to do so.

This is also true of the waste disposal and vent system.

