September 25, 2007

Mr. Frank Milbourn

Associated Contractors

1340 Poydras Street, Ste 1810

New Orleans, LA  70112

VIA FACSIMILE:
504-962-3344

RE:
 Concourse “C,” Moissant Airport, New Orleans, Louisiana

Dear Mr. Milbourn,

As you requested, I have looked at drawing S-54 & S-135 of the original Moissant design drawings, that are basically roof drawings, but have a section of the concourse floor shown also.

With the little bit shown, I surmise that the floor is 3,000 psi concrete on regular corrugated decking.  The thickness of the slab above the decking is four inches.  Thus, with the ribs, the concrete is probably five and one half inches deep.  The spacing of floor beams is four feet three inches.

The equipment you plan to use weighs 16,000 lbs distributed on four wheels that will provide a 35 psi bearing pressure.  The wheel base is essentially six feet and width is the same.

This being the case, no floor panel should have to support more than two tires at one time, and the wheel loads on any panel will be approximately six feet apart.

Under these conditions, the 450 series JLG lift should not present a problem to the structure, but it should be noted that the drawings furnished me were vague and mostly applied to the roof.  The floor deck was more of an indication than a design drawing.

Sincerely,

Emmett G. (Pete) Dammon, P.E.
La. License No. 8796
