Notes:
1.  240.4(B) Devices Rated 800 Amperes or Less. The next higher standard overcurrent device rating (above the ampacity of the conductors being protected) shall be permitted to be used, provided all of the following conditions are met: (1) The conductors being protected are not part of a multioutlet branch circuit supplying receptacles for cord and- plug-connected portable loads.  Also see Table 210.24 and Section 210.23.
240.4(C) Devices Rated Over 800 Amperes. Where the overcurrent device is rated over 800 amperes, the ampacity of the conductors it protects shall be equal to or greater than the rating of the overcurrent device defined in 240.6.
2.  Neutral Conductor. (a) A neutral conductor that carries only the unbalanced current from other conductors of the same circuit shall not be required to be counted as a current carrying conductor.
(b) In a 3-wire circuit consisting of two phase wires and the neutral of a 4-wire, 3-phase, wye-connected system, a common conductor carries approximately the same current as the line-to-neutral load currents of the other conductors and shall be counted as a current carrying conductor.
(c) On a 4-wire, 3-phase wye circuit where the major portion (over 50 per cent) of the load consists of nonlinear loads such as electric discharge lighting and computer loads, harmonic currents are present in the neutral conductor and the neutral shall be considered a current carrying conductor.
(d) Each current-carrying conductor of a paralleled set of conductors shall be counted as a current carrying conductor.
3.  Termination provisions of equipment for circuits rated 100 amperes or less, or marked for 14 AWG through 1 AWG conductors, shall be used only for one of the following: 
(1) Conductors rated 60°C (140°F).
(2) Conductors with higher temperature ratings, provided the ampacity of such conductors is determined based on the 60°C (140°F) ampacity of the conductor size used.
(3) Conductors with higher temperature ratings if the equipment is listed and identified for use with such conductors.
(4) For motors marked with design letters B, C, or D, conductors having an insulation rating of 75°C (167°F) or higher shall be permitted to be used, provided the ampacity of such conductors does not exceed the 75°C (167°F) ampacity.
Termination provisions of equipment for circuits rated over 100 amperes, or marked for conductors larger than 1 AWG, shall be used only for one of the following:
(1) Conductors rated 75°C (167°F)
(2) Conductors with higher temperature ratings, provided the ampacity of such conductors does not exceed the 75°C (167°F) ampacity of the conductor size used, or up to their ampacity if the equipment is listed and identified for use with such conductors.
Author's Note:  In general most terminals are rated for 75 degrees C.  Conductors with 90 degree C insulations can be used on these terminals provided they are not used at an ampacity higher than the 75 degree C. ampacity.   However, the 90 degree insulation ampacity can be used for derating purposes.    For example a No. 12 AWG copper 90 degree C. THHN rated at 30 amperes can be used in a raceway with up to 9 current carrying conductors on a 20 ampere circuit breaker since the  derated  ampacity is 0.7 x 30 = 21 amperes.
75 degree terminations may be stamped as AL7CU.
4.  Conductors in Parallel. Aluminum, copper-clad aluminum, or copper conductors of size 1/0 AWG and larger, comprising each phase, polarity, neutral, or grounded circuit conductor, shall be permitted to be connectedin parallel (electrically joined at both ends).
5.  Where parallel conductors are run in separate raceways or cables, the raceways or cables shall have the same physical characteristics.  Where conductors are in separate raceways or cables, the same number of conductors shall be used in each raceway or cable. Conductors of one phase, polarity, neutral, or grounded circuit conductor shall not be required to have the same physical characteristics as those of another phase, polarity, neutral, or grounded circuit conductor to achieve balance.
6.  Where conductors are run in parallel in multiple raceways or cables as permitted in NEC Section 310.4, the equipment grounding conductors, where used, shall be run in parallel in each raceway or cable.
The size of the equipment grounding conductor shall be based on 1 or 2 below:

Electrician2.com
