	[image: image1.png]



	PROPOSAL

	GULF COAST ELECTRIC CO. LLC
Serving the Gulf Coast
	

	1095 FLORIDA AVE., SLIDELL, LA 70458
Phone 985-649-5832 Fax 985-641-5950
gulfcoastelect@bellsouth.net
	      LA License 46737


	to
	Kevin Vernor
CRM Company
4455 American Way
Baton Rouge, La 70816
225-295-4262  F 225-295-7640
	

	DATE
	
	Location

	1/26/07
	
	ATT I10 Service Rd Slidell


	item 
	
	description
	Labor
	Material
	line total

	1
	
	Service call on Friday (01/22/10) at 6:30 PM to the ATT office in Slidell on the I-10 Service Rd. Found marine aluminum cables feeding the manual transfer switch burned at the connectors in the transfer switch. Solution was to disconnect the transfer switch from the main feed and reconnect at the panel. Work was completed and store back on line at 8:00 PM.
	
	
	

	2
	
	Permanente Solution: Replace all aluminum cables feeding the transfer switch with 3/0 copper cables. Replacement of the wire can be completed in the day time. The reconnection of the transfer switch to the main feed will be completed after the store closes. 
	
	
	

	3
	
	
	
	
	

	4
	
	service call on 01/22/10
	160.00
	
	160.00

	5
	
	Replace 3/0 cables and reconnect
	320.00
	100.00
	420.00

	6
	
	
	
	
	

	7
	
	
	
	
	

	8
	
	
	
	
	

	9
	
	
	
	
	

	Terms: invoices to be paid with-in 5 days of receipt.
	
	

	
	
	

	Accepted by:
	Sales Tax
	

	Date:
	Total
	580.00


Thank you for your business!







