David Dammon
ENCE 4358
Design Wind Bracing Between Framing Columns 3N & 4N (Similar between 3O and 4O)

Assumptions : Fy = 50ksi Fu = 65ksi (Typical L shape is A36)

Level 1 to Level 2 - Using same design for L2 to L3 and L3 to L4.

Designed bracing to resist “tension only” due to Wind loads, Row N resists 50% of the East/West wind load and row O resists 50% of the load. Each bracing will not support any gravity loads. Assume that the East/West wind produces 40 psf.

East or West Building Area - from mid height on Level 1 to Level 6
Area between column rows * 3 plus 1 ft each side of columns rows times 3 ½ floors + 3 ft parapet. Add this to the area of Level 6. Multiply all of this by the force

[(3 * 24) + 2] * [(3.5 * 14 )+ 3] + 13 (24 +2)
= [(74) * (52)] + [13 * 26] = 3848 + 338 = 4186 ft2 * 40 #/ft2 = 167440 or 167.4 k

Each row of columns N and O will withstand ½ of the wind 167.4 / 2 = 83.7 k

Length of the diagonal = √(332 + 142) = √1285 = 35.85 ft

Each diagonal tension force = ratio * force = 35.85'/33' * 83.7 k = 90.9 k (t)

Gross section yielding

Pn = Fy x Ag

LRFD Φt=0.90 & Load = 1.6W	ASD Ωt=1.67 & Load = 1.0W
Load = Φt * Pn = Φt * Fy x Ag	Load = Pn/ Ωt = Fy * Ag/Ωt
Ag = Load/ Φt * Fy	Ag = Load * Ωt / Fy
Ag = 90.9 k * 1.6 /(0.9 * 50ksi)	Ag = 90.9 k * 1.67/50ksi
Ag = 145.44 k /45 ksi = 3.23 in2	Ag = 151.8/50ksi = 3.04in2

Tensile rupture strength
     Pn = Fu * Ae

LRFD Φt=0.75	ASD Ωt=2.00
Load = Φt * Pn = Φt * Fu * Ae	Load = Pn/ Ωt = Fu * Ae/ Ωt
Ae = Load/Φt * Fu	Ae= Load * Ωt /Fu
Ae = 90.9 k /0.75 * 65ksi	Ae= 90.9 k * 2/65ksi
Ae = 90.9 k /48.75ksi = 1.86in2	Ae= 181.8k /65ksi = 2.80in2

rx,y minimum= L/300	rx,y minimum= L/300
rx,y= 35.85 ft * 12 in/ft/300	rx,y = 430.2/300 = 1.434

Try L shape bracing:
L6x6x3/8	Wt. 14.9 #/ft	Ag = 4.38 in2	r = 1.87 in

For ¾” A325-N bolts	LRFD Capacity 15.9 k/bolt	ASD Capacity 10.6 k/bolt

LRFD	ASD
Diagonal Force/bolt Capacity 145.44 k /15.9 k = 9.1 bolts 90.9 k / 10.6 k = 8.6 bolts
Use two lines of 5 bolts
Table D3.1 AISC Case 8 Single angle with more than 4 fasteners per line use U = 0.80

Ae = U * An = 0.8 [4.38 in2 – 2(3/8”) (3/4” + 1/8”)] = 0.8 [4.38 – 0.656] = 0.8 * 3.723 = 2.98 in2
This Ae meets the Tensile Rupture Strength requirements calculated with ASD.

Level 4 to Level 5 - Both tension and compression.

Designed bracing to resist “both tension and compression” due to Wind loads, Row N resists 50% of the East/West wind load and row O resists 50% of the load. Each bracing will not support any gravity loads. Assume that the East/West wind produces 40 psf.

East or West Building Area - from mid height on Level 4 to Level 6

[(3 * 24) + 2] * (16/2 +3) + 13 (24 +2)
= [(74) * (11)] + [13 * 26] = 814 + 338 = 1152 ft2 * 40 #/ft2 = 46080 or 46.1 k

Each row of columns N and O will withstand ½ of the wind 46.1 / 2 = 23.1 k

Length of the diagonal = √(332 + 142) = √1285 = 35.85 ft

Each diagonal force = ratio * force = 35.85'/33' * 23.1 k = 25.1 k (t & c)
ASD = 25.1k (t & c)	LRFD = 1.6 * 25.1k = 40.2k (t & c)
AISC Pg 4-54 , KL shown at 36' - HSS 7x7x3/16 ASD= 29.0 LRFD = 43.6

KL/r = 200	r = KL/200	r = (1)*(35.85')*(12”/')/200 = 2.15”

Try HSS 7 x 7 x 3/16; A=4.67 in2; r=2.77 in; Fy = 46 ksi Wt = 17.06 #/ft (AISC pg 1-53)

Check Kl/r = (1)*(35.85')*(12”/')/2.77 = 155.3
Fe = (π2 * 29,000) / (155.3)2 = 11.87 ksi < .44*(46 ksi)=20.2 ksi	ELASTIC
Fcr = .877 Fe = .877 * 11.87 ksi = 10.41 ksi	Pn = Fcr x Ag

LRFD Φc=0.90	ASD Ωc=1.67
Φc x Pn	Pn/ Ωc
0.9 * 10.41 ksi * 4.67 = 43.7k 10.41 ksi * 4.67 in2/1.67 = 29.1k
    Check Required/Capacity	40.2/43.7	25.1/29.1

Use same HSS 7 x 7 x 3/16 for Level 5 to Level 6
Column Design

Assumptions : Fy = 50ksi Fu = 65ksi
Dead Load : 100 psf
Exterior Wall System : 50 psf (Supported mid-height of each floor)
Live Load : L2, L3, L4 = 120 psf
 L5, L6 (Lr) = 60 psf
Wind Load: 40 psf (Service Level)
Seismic Load: None

Exterior non-corner columns - M2, M3, M4, M5, P2, P3, P4, P5, N1, N6, O1, O6
Exterior corner columns - M1, M6, P1, P6 all have lower loads but use same section as Exterior non-corner columns.
Non Rigid Frame Column Splice: Mid-Height between Level 2 and Level 3 only, from this splice to top is single unit.
ASD load cases	D + L	&	D + .75L + .75Lr
LRFD load cases	1.2D + 1.6L + 0.5Lr

Exterior non-corner Column Area per level 33'(24'/2) = 33' (12') = 396 ft2

Design Load above Splice for Exterior Non-Corner Columns : L3 + L4 + L5
D: [396 ft2 (100 psf + 100 psf + 100 psf)] + [33' * (14' + 14' + 10') * (50 psf)]
=118,800 + 62,700 =181,500 or 181.5k
L: [396 ft2 (120 psf + 120 psf)] = 95,040k or 95.0k
Lr : 396 ft2 (60 psf) = 23,760k or 23.8k

ASD load cases	D + L = 181.5k + 95.0k = 276.5k *** USE THIS LOAD ***
D + .75L + .75Lr = 181.5k + [.75 * (95.0k)] + [.75 * (23.8k)]
= 181.5k + 71.3k + 17.9k = 270.7k
LRFD load cases	1.2D + 1.6L + 0.5Lr = [1.2 * 181.5k] + [1.6 * (95.0k)] + [0.5 * (23.8k)]
= 217.8k + 152.0k + 11.9k = 381.7k *** USE THIS LOAD ***

Above Splice ASD & LRFD :
AISC 13th Pg 4-14; KL=14'; W14x61 (50 ksi)	ASD Pn/ Ωc = 380k > 276.5k OK
LRFD Φc x Pn = 572k > 381.7k OK
AISC 13th Pg 4-14; KL=14'; W14x53 (50 ksi)	ASD Pn/ Ωc = 267k not > 276.5k NOT OK
LRFD Φc x Pn = 401k > 381.7k OK

Check From Above Splice W14x61 with KL=14'
ry = 2.45”; Area = 17.9 in2; AISC Pg 1-22
Kl/r = (1)*(14')*(12”/')/2.45 = 68.6
Fe = (π2 * 29,000) / (68.6)2 = 60.82 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 50/60.82)	*50 = (0.6580.82209) * 50	= 35.44 ksi	Pn = Fcr x Ag
LRFD Φc=0.90	ASD Ωc=1.67
Φc x Pn	Pn/ Ωc
0.9 * 35.44 ksi * 17.9 in2 = 570.9k 35.44 ksi * 17.9 in2/1.67 = 379.9k
    Check Required/Capacity	382/571	277/380

Design Load from Base to Splice :	L1 + L2 + L3 + L4 + L5 (L1 Supported by Foundation)
D: [396 ft2 (100 psf + 100 psf + 100 psf + 100 psf)] + [33' * (14' + 14' + 14' + 10') * (50 psf)]
=158,400 + 85,800 =244,200 or 244.2k
L: [396 ft2 (120 psf + 120 psf + 120 psf )] = 142,560k or 142.6k
Lr : 396 ft2 (60 psf) = 23.8k

ASD load cases	D + L = 244.2k + 142.6k = 386.8k *** USE THIS LOAD ***
D + .75L + .75Lr = 244.2k + [.75 * (142.6k)] + [.75 * (23.8k)]
= 244.2k + 107.0k + 17.85k = 369.1k
LRFD load cases	1.2D + 1.6L + 0.5Lr = [1.2 * (244.2k)] + [1.6 * (142.6k )] + [0.5 * (23.8k)]
= 293.04k + 228.15k + 11.9k = 533.1k *** USE THIS LOAD ***
From Base to Splice ASD & LRFD :
AISC 13th Pg 4-14; KL=14'; W14x68 (50 ksi)	ASD Pn/ Ωc = 425k > 387k OK
LRFD Φc x Pn = 639k > 533k OK
AISC 13th Pg 4-14; KL=14'; W14x61 (50 ksi)	ASD Pn/ Ωc = 380k NOT> 387k NOT OK
LRFD Φc x Pn = 572k > 533k OK

Check From Base to Splice W14x68 with KL=14'
ry = 2.46”; Area = 20.0 in2; AISC Pg 1-22
Kl/r = (1)*(14')*(12”/')/2.46 = 68.3
Fe = (π2 * 29,000) / (68.3)2 = 61.4 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 ^50/61.4)	* 50 = (0.6580.81433) * 50 = 35.56 ksi	Pn = Fcr x Ag

LRFD Φc=0.90	ASD Ωc=1.67
Φc x Pn	Pn/ Ωc
0.9 * 35.56 ksi * 20.0 in2 = 640.1k 35.56 ksi * 20.0 in2/1.67 = 425.9k
    Check Required/Capacity	533/640	387/426

CONCLUSION	Exterior Columns (Non-Corners) Above Splice use W14x61 (50 ksi)
Exterior Columns (Non-Corners) from Base to Splice use W14x68 (50 ksi)

Design Interior Columns : N3; N4; O3; O4
Splices 4 ft above L2 and 4 ft above L4 ; Column Area per level = 24' * 33' = 792 ft2

Dead Loads (D)
Above L4 Splice #1 - (L5)[792 ft2 * 100 psf] + (L6)[396 ft2 * 100 psf] + (Ext Wall)[13' * 33' * 50 psf]
     79,200 + 39,600 + 21,450 = 140,250 or 140.2k
Above L2 Splice #2 - 140.2k + [2 * (792 ft2 * 100 psf)] = 298.6k
Base above L1 - 298.6k * [792 ft2 * 100 psf] = 377.8k

Floor Live Loads (L)
Above L4 Splice #1 - (L5)[396 ft2 * 120 psf] = 47.5k
Above L2 Splice #2 - (L5)47.5k + (L3 & L4) [2 * (792 ft2 * 120 psf)] = 237.6k
Base above L1 - 237.6k * [792 ft2 * 60 psf] = 285.1k

Roof Live Load (Lr)
Above L4 Splice #1 - [792 ft2 * 60 psf] = 47.5k
Above L2 Splice #2 -	= 47.5k
Base above L1 -	= 47.5k

Wind Load :	Splice #1 : [(3.6k * 22') + (18k * 10')] / 33' = 7.9k
Splice #2 : [(3.6k * 50') + (18k * 38') + (20.2k * (24' + 10')] / 33' = 47.0k
Base : [(3.6k * 68') + (18k * 56') + (20.2k * (18' + 28' + 42')] / 33' = 91.8k
ASD load cases	D + L ; D + Lr; .6D + W; D + W

Splice #1	D + L ; 140.2k © + 47.5k © = 187.7k ©
D + Lr; 140.2k © + 47.5k © = 187.7k © *** USE THIS LOAD ***
.6D + W; 0.6 * 140.2k © + 7.9k (T) = 76.2k ©
.6D + W; 0.6 * 140.2k © + 7.9k © = 92.0k ©
D + W; 140.2k © + 7.9k (T) = 132.3k ©
D + W; 140.2k © + 7.9k © = 148.1k ©

Splice #2	D + L ; 298.6k © + 237.6k © = 536.2k © *** USE THIS LOAD ***
D + Lr; 298.6k © + 47.5k © = 346.1k ©
.6D + W; 0.6 * 298.6k © + 47.0k (T) = 132.2k ©
.6D + W; 0.6 * 298.6k © + 47.0k © = 226.2k ©
D + W; 298.6k © + 47.0k (T) = 251.6k ©
D + W; 298.6k © + 47.0k © = 345.6k ©

Base	D + L ; 377.8k © + 285.1k © = 662.9k © *** USE THIS LOAD ***
D + Lr; 377.8k © + 47.5k © = 425.3k ©
.6D + W; 0.6 * 377.8k © + 91.8k (T) = 139.9k ©
.6D + W; 0.6 * 377.8k © + 91.8k © = 318.5k ©
D + W; 377.8k © + 91.8k (T) = 286.0k ©
D + W; 377.8k © + 91.8k © = 469.6k ©

ASD Analysis	Splice #1	187.7k @ KL=14	W14x43 Pn= 212k
Splice #2	536.2k @ KL=14	W14x90 Pn= 682k
Base	662.9k @ KL=14	W14x99 Pn= 751k

LRFD load cases	1.2D + 1.6L + 0.5Lr ; 1.2D + 0.5L + 1.6Lr ;
0.9D + 1.6W ; 1.2D + 1.6W + 0.5(L + Lr )

Splice #1	1.2D + 1.6L + 0.5Lr; 1.2(140.2k ©) + 1.6(47.5k ©) + 0.5(47.5k ©) = 268.0k ©
1.2D + 0.5L + 1.6Lr; 1.2(140.2k ©) + 0.5(47.5k ©) + 1.6(47.5k ©) = 268.0k © * USE THIS LOAD *
0.9D + 1.6W; 0.9(140.2k ©) + 1.6(7.9k (T)) = 113.5k ©
0.9D + 1.6W; 0.9(140.2k ©) + 1.6(7.9k ©) = 138.8k ©
1.2D + 1.6W + 0.5(L + Lr ); 1.2(140.2k ©) + 1.6(7.9k (T)) + 0.5(47.5k © + 47.5k ©) = 203.1k ©
1.2D + 1.6W + 0.5(L + Lr ); 1.2(140.2k ©) + 1.6(7.9k ©) + 0.5(47.5k © + 47.5k ©) = 228.4k ©

Splice #2	1.2D + 1.6L + 0.5Lr; 1.2( 298.6k ©) + 1.6( 237.6k ©) + 0.5(47.5k ©) =762.2 k ©*USE THIS LOAD *
1.2D + 0.5L + 1.6Lr; 1.2( 298.6k ©) + 0.5( 237.6k ©) + 1.6(47.5k ©) = 553.1k ©
0.9D + 1.6W; 0.9( 298.6k ©) + 1.6(47.0k (T)) = 193.5 k ©
0.9D + 1.6W; 0.9( 298.6k ©) + 1.6(47.0k ©) = 343.94 k ©
1.2D + 1.6W + 0.5(L + Lr ); 1.2( 298.6k ©) + 1.6(47.0k (T)) + 0.5(237.6k © + 47.5k ©) =425.7 k ©
1.2D + 1.6W + 0.5(L + Lr ); 1.2( 298.6k ©) + 1.6(47.0k ©) + 0.5(237.6k © + 47.5k ©) =576.1k ©

Base	1.2D + 1.6L + 0.5Lr; 1.2( 377.8k ©) + 1.6( 285.1k ©) + 0.5(47.5k ©) =933.3k © *USE THIS LOAD *
1.2D + 0.5L + 1.6Lr; 1.2( 377.8k ©) + 0.5( 285.1k ©) + 1.6(47.5k ©) =671.9k ©
0.9D + 1.6W; 0.9( 377.8k ©) + 1.6(91.8k (T)) = 193.1k ©
0.9D + 1.6W; 0.9( 377.8k ©) + 1.6(91.8k ©) = 486.9k ©
1.2D + 1.6W + 0.5(L + Lr ); 1.2( 377.8k ©) + 1.6(91.8k (T)) + 0.5(285.1k © + 47.5k ©) =472.8 k ©
1.2D + 1.6W + 0.5(L + Lr ); 1.2( 377.8k ©) + 1.6(91.8k ©) + 0.5(285.1k © + 47.5k ©) =766.5 k ©

LRFD	ASD
Splice #1	Pn = 268.0k ©	Splice #1	Pn = 187.7k ©
KL=14	W14x43	KL=14	W14x43

Splice #2	Pn = 762.2 k ©	Splice #2	Pn = 536.2k ©
KL=14	W14x82	KL=14	W14x90

Base	Pn = 933.3k ©	Base	Pn = 662.9k ©
KL-14	W14x90	KL=14	W14x90

Check Above Splice #1 W14x43 with KL=14'
ry = 1.89”; Area = 12.6 in2; AISC Pg 1-22
Kl/r = (1)*(14')*(12”/1')/1.89 = 88.9
Fe = (π2 * 29,000) / (88.9)2 = 36.2 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 ^50/36.2)	* 50 = (0.6581.38122) * 50 = 28.05 ksi	Pn = Fcr x Ag

LRFD Φc=0.90	ASD Ωc=1.67
Φc x Pn	Pn/ Ωc
0.9 * 28.05 ksi * 12.6 in2 = 318.1k 28.05 ksi * 12.6 in2/1.67 = 211.6k
    Check Required/Capacity	268/318	188/212

Check Above Splice #2 W14x90 with KL=14'
ry = 3.70”; Area = 26.5 in2; AISC Pg 1-22
Kl/r = (1)*(14')*(12”/')/3.70 = 45.4
Fe = (π2 * 29,000) / (45.4)2 = 138.9 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 ^50/138.9)	* 50 = (0.6580.35997) * 50 = 43.01 ksi	Pn = Fcr x Ag

LRFD Φc=0.90	ASD Ωc=1.67
Φc x Pn	Pn/ Ωc
0.9 * 43.01 ksi * 26.5 in2 = 1025.8k 43.01 ksi * 26.5 in2/1.67 = 682.5k
    Check Required/Capacity	762/1026	536/682

Check Above Base W14x90 with KL=14'
ry = 3.70”; Area = 26.5 in2; AISC Pg 1-22
Kl/r = (1)*(14')*(12”/')/3.70 = 45.4
Fe = (π2 * 29,000) / (45.4)2 = 138.9 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 ^50/138.9)	* 50 = (0.6580.35997) * 50 = 43.01 ksi	Pn = Fcr x Ag

LRFD Φc=0.90	ASD Ωc=1.67
Φc x Pn	Pn/ Ωc
0.9 * 43.01 ksi * 26.5 in2 = 1025.8k 43.01 ksi * 26.5 in2/1.67 = 682.5k
    Check Required/Capacity	933/1026	663/682

CONCLUSION	Interior Columns (N3;N4; O3; O4)
Above Splice #1 W14x43
Above Splice #2 to Splice #1 W14x90

Floor Beam Design for North/South Interior Beams Level 2, Level 3 & Level 4

Contributory Width = 33/3 = 11 ft
Mmax = wL2/8 , Vmax = wL/2 , Δmax= 5wL4/384EI (AISC Pg 3-220)
Deflection Limits, For ASD & LRFD use un-factored loads
ΔLive < 24*12/360 = 0.8 in ; ΔTotal < 24*12/200 = 1.44 in
LOADS
wD=100psf * 11' = 1.1k/LF	wnD = 1.2 * 1.1k/LF = 1.32k/LF
wL=120psf * 11' = 1.32k/LF	wnL = 1.6 * 1.32k/LF = 2.11k/LF
  wT = 2.42k/LF	wnT = 3.43k/LF

Imin = max of 5wLL4 *1728/384E*ΔLive or	5 wT L4 *1728/384E* ΔTotal
Imin = max of (5 * 1.32k/LF * 244 * 1728) or	(5 * 2.42k/LF * 244 * 1728)
    (384 * 29,000 * 0.8 in)	(384 * 29000 * 1.44)
      = max of (425 in4)	or	(433 in4)
Imin = 433 in4

Designed as fully braced
Mn = Mp = ZFy

LRFD	ASD
Load Case 1.2D + 1.6L	Load Case D + L
Mmax = 1/8 * 3.43 * 242 = 247.0ft-k	Mmax = 1/8 * 2.42 * 242 = 174.2ft-k
Vmax = 3.43 * 24 /2 = 41.2k	Vmax = 2.42 * 24 /2 = 29.0k
Zrequired = 247 *12”/ft /(.9 * 50ksi) = 65.9in3	Zrequired = 174.2 *12”/ft * 1.67 / 50ksi = 69.8in3
Irequired = 433 in4	Irequired = 433 in4

W18x35 A=10.3, d=17.7, tw=0.300, Zx-x = 66.5 >64, Ix-x = 510 > 433
Check shear: LRFD (d * tw * ksi) > Vmax ;	ASD (d * tw * ksi/1.5) > Vmax
LRFD (17.7 * 0.3 * 50) = 265 > 41.2 ;	ASD (17.7 * 0.3 * 50/1.5) = 177 > 29.0

Floor Beam Design for North/South Exterior Beams Level 2, Level 3 & Level 4 (Cont.)

Contributory width floor = 11/2 = 5.5'
Contributory height exterior walls = 14'

wD=(100psf * 5.5') + (50psf * 14')	= 1.25k/LF	wnD = 1.2 * 1.25k/LF = 1.50k/LF
wL=(120psf * 5.5'	= 0.66k/LF	wnL = 1.6 * 0.66k/LF = 1.06k/LF
  wT = 1.91k/LF< 2.42k/LF (Interior)	wnT = 2.56k/LF < 3.43k/LF (Interior)
Use W18x35 for both ASD and LRFD

Beam End Connections

¾” A325-N bolts	LRFD Capacity 15.9 k/bolt	ASD Capacity 10.6 k/bolt

East/West Girders Interior Level 2, Level 3 & Level 4

LOADS
PD=100psf * 11' * 24'= 26.4k	ΔLive = 33 * 12/360 = 1.1
PL=120psf * 11' * 24'= 31.7k	ΔTotal = 33 * 12/200 = 1.98
  PT = 58.1k

Imin = max of 0.036 PLL3 *1728/E *ΔLive or	0.036 PT L3 *1728/E * ΔTotal
Imin = max of ( 0.036 * 31.7k * 243 * 1728) or	( 0.036 * 58.1k * 243 * 1728)
      (29,000 * 1.1 in)	(29,000 * 1.98)
      = max of (855 in4)	or	(870 in4)
Imin = 870 in4

Mmax = P (L/3)
Vmax = P
Δmax = 0.036 PL3/EI (AISC Pg 3-208)

LRFD	ASD
Mnmax = (1.2PD + 1.6PL) * 33'/3	Mmax = PT (33'/3)
  = [1.2(26.4k) + 1.6(31.7k)] * 33/3 = 906.4ft-k	= 58.1k (33/3) = 639.1ft-k
Vnmax = (1.2PD + 1.6PL)	Vmax = PT
    = [1.2(26.4k) + 1.6(31.7k)] = 82.4k	= 58.1k
Zrequired = 906.4ft-k *12”/ft /(.9 * 50ksi) = 242in3	Zrequired = 639.1ft-k *12”/ft * 1.67 / 50ksi = 256in3
Irequired = 870 in4	Irequired = 870 in4

W21x101 A=29.8, d=21.4, tw=0.500, ;	W21x111 A=32.7, d=21.5, tw=0.550,
Zx-x = 253 >242, Ix-x = 2420 > 870 ;	Zx-x = 279 >256, Ix-x = 2670 > 870
Check shear: LRFD (d * tw * ksi) > Vnmax ;	ASD (d * tw * ksi/1.5) > Vmax
( 21.4 * 0.5 * 50) = 535 > 82.4	;	( 21.5 * 0.55 * 50/1.5) = 394 > 58.1

East/West Girders Exteriors Level 2, Level 3 & Level 4

Contributory width floor = 24'/2 = 12'
Contributory height exterior walls = 14' * 11'

PD=(100psf * 12' * 11') + (50psf * 14' * 11')	= 20.9k	PnD = 1.2 * 20.9k = 25.1k
PL=(120psf * 12' * 11')	= 15.8k	PnL = 1.6 * 15.8k = 25.3k
  PT = 36.7k	PnT = 50.4k

Imin = max of 0.036 PLL3 *1728/E *ΔLive or	0.036 PT L3 *1728/E * ΔTotal
Imin = max of ( 0.036 * 15.8k * 243 * 1728) or	( 0.036 * 36.7k * 243 * 1728)
      (29,000 * 1.1 in)	(29,000 * 1.98)
      = max of (425.9 in4)	or	(549.6in4)
Imin = 549.6 in4

Mmax = P (L/3)
Vmax = P
Δmax = 0.036 PL3/EI (AISC Pg 3-208)

LRFD	ASD
Mnmax = (1.2PD + 1.6PL) * 33'/3	Mmax = PT (33'/3)
  = [25.1k + 25.3k] * 11' = 554.4ft-k	= 36.7k (11') = 403.7ft-k
Vnmax = (1.2PD + 1.6PL) = 50.4k	Vmax = PT = 36.7k
Zrequired = 554.4ft-k*12”/ft /(.9 * 50ksi) = 147.8in3	Zrequired = 403.7ft-k *12”/ft * 1.67 / 50ksi = 161.8in3
Irequired = 549.6 in4	Irequired = 549.6 in4

W21x68 A=20.0, d=21.1, tw=0.4300,	W21x73 A=21.5, d=21.2, tw=0.455,
Zx-x = 160 >147.8, Ix-x = 1480 > 549.6	Zx-x = 172 >161.8, Ix-x = 1600 > 549.6
Check shear: LRFD (d * tw * ksi) > Vnmax	ASD (d * tw * ksi/1.5) > Vmax
LRFD ( 21.1 * 0.43 * 50) = 454 > 50.4 ;	ASD ( 21.2 * 0.455 * 50/1.5) = 321 > 36.7

RIGID FRAME DESIGN @ N2 – O2 & N5 - O5
Resisting North/South Wind Loads & Providing North/South Stability

P-loads – Lump all vertical loads at end nodes, even though some load goes directly to rigid frame beams.
LRFD Load Case 1.6D + 1.2Wind + 0.5L
E = 29,000 ksi
Wind Loads
W1 = 1.6 * Wind psf [½ length of building * height of exterior wall supported by each floor]
W1 = 1.6 * 40psf [(½(5 * 33' + 2')) * 14')]
      = 1.6 * 40psf [(½ * 167') * 14'] = 1.6 * 40psf * 1169ft2 = 74.8k

W2 = 1.6 * Wind psf [½ (length of building * ½ height of exterior wall supported by each floor + parapet) + (½ length of the penthouse + 1') * ½ height of exterior wall penthouse]
W2 = 1.6 * 40psf [[(½(5 * 33' + 2')) * (14/2' + 3')] + [½(3 * 33' + 2' ) * 12'/2]]
W2 = 1.6 * 40psf [[(½ * 167') * 10'] + [(50.5' * 6')]] = 1.6 * 40psf [835ft2 + 303ft2] = 72.8k

W3 = 1.6 * Wind psf [½ length of the penthouse + 1') * ½ height of exterior wall penthouse +1' parapet]
W3 = 1.6 * 40psf [½(3 * 33' + 2' ) * (12'/2 + 1')]
W3 = 1.6 * 40psf [50.5' * 7'] = 1.6 * 40psf * 353.5ft2 = 22.6k

Vertical Loads from 1.2D + 0.5L
P1 = 1.2 * [24' * 33' * 100psf] + 0.5[24' * 33' * 120psf]
    = 95.04k + 47.52k = 142.56k

P2 = 1.2[(24' * 33' * 100psf)+(6'(12' + 16.5') *50psf)] + 0.5 [24' * 33' *60psf]
    = 1.2 [79.2k + 8.55k] + 0.5 [47.5k] = 105.3k + 23.7k = 129.0k

P3 = 1.2 [(12' * 16.5' * 100psf) + ((6'+1')(12' + 16.5') * 50psf)] + 0.5 [12' * 16.5' * 60psf]
    = 1.2 [19.8k + 10.0k] + 0.5 [11.9k] = 35.76k + 5.95k = 41.7k

All factored load at Level 2, 3, or 4 for 50% of Bldg not directly applied to rigid frame as P4. Cut the building in two symmetrical halves North to South, each half of building is supported by rigid frame in that area: 72' x 82.5' = 5,940 ft2 , with perimeter : (2 * 82.5') + 72' = 237' ; Penthouse dimensions 24' x 49.5' = 1,188 ft2 , with perimeter : (2 * 49.5') + 24' =123'
P4 = 1.2 [(5,940 ft2 * 100 psf) + (14' * 237' * 50psf)] + 0.5 [5,940 ft2 * 120 psf] – 2 * P1
    = 1.2 [594k + 165.9k] + 0.5 [712.8k] – 2 [142.6k] = 911.88k + 356.4k – 285.2k = 983.1k

P5 = 1.2[(5,940 ft2 *100 psf)+((7' + 3') *237' *50psf)+(6' *123' *50psf)]+0.5[5,940 ft2 *60 psf]– 2 * P2
    = 1.2 [594k + 118.5k + 36.9k] + 0.5 [356.4k] – 2 [129k] = 899.3k + 178.2k – 258.0k = 819.5k

P6 = 1.2[(1,188 ft2 *100 psf) + ((6' + 1') * 123' * 50psf)] + 0.5[1,188 ft2 * 60 psf] – 2 * P3
    = 1.2 [118.8k + 43.0k] + 0.5 [71.3k] – 2 [41.7k] = 194.2k + 35.7k – 83.4k = 146.5k

Preliminary Design – Portal Method, ignoring P–Δ

L5 – L6 Columns and L6 Beam
M = 12'/2 * 11.3k = 67.8ft-k

L4 – L5 Columns	L5 Beam
M = 14'/2 * 47.7k = 333.9ft-k	333.9ft-k + 67.8ft-k = 401.7ft-k

L3 – L4 Columns	L4 Beam
M = 14'/2 * 85.1k = 595.7ft-k	595.7ft-k + 333.9ft-k = 929.7ft-k

L2 – L3 Columns	L3 Beam
M = 14'/2 * 122.5k = 857.5ft-k	857.5ft-k + 595.7ft-k = 1453.2ft-k

L1 – L2 Columns	L2 Beam
M = 14'/2 * 159.9k = 1119.3ft-k	1119.3ft-k + 857.5ft-k = 1976.8ft-k

Rigid Frame Beam Selection
Ignoring Axial Force and P–Δ ; Assumed fully braced

L6 Zrequired = (67.8ft-k) * (12”/ft) / (.9 * 50ksi) = 18.1 in3	W14x68, Z=115 in3
L5 Zrequired = (401.7ft-k) * (12”/ft) / (.9 * 50ksi) = 107.1 in3	W21x83, Z=196 in3
L4 Zrequired = (929.7ft-k) * (12”/ft) / (.9 * 50ksi) = 247.9 in3	W21x132, Z=333 in3
L3 Zrequired = (1453.2ft-k) * (12”/ft) / (.9 * 50ksi) = 387.5 in3	W30x148, Z=500 in3
L2 Zrequired = (1976.8ft-k) * (12”/ft) / (.9 * 50ksi) = 527.1 in3	W30x191, Z=675 in3

In addition to the strength requirements limit the L6 lateral movement to height/150 due to factored loads, including P–Δ, 816” / 150 = 5.44”

Rigid Frame Preliminary Column Design

Below Splice #2 to Column Base (L1 – L2)

Mprelim = 1119.3ft-k
Forces at base of L1 due to Wind = [W1 * (distance from base to Level 2 + Level 3 + Level 4) + (W2 * distance from base to Level 5) + (W3 * distance from base to Level 6) ] / distance between rigid frame columns
    = [74.8k * (14' + 28' + 42') + (72.8k * 56') + (22.6k * 68')] / 24'
    = [ 6283.2ft-k + 4076.8ft-k + 1536.8ft-k ] / 24' = 495.7k (due to 1.6W)

PDown = 3P1 + P2 + P3 + Axial force from wind overturning
PDown = 3(142.56k) + 129.0k + 41.7k + 495.7k = 1094.1k
(Note: Pmin = .9PDown = 984.7k> 495.5k therefore No Uplift)

At this point assuming Mn = Mprelim
Using this Moment only Zrequired = (1119.3ft-k * 12”/ft) / (.9 * 50ksi) = 298.9 in3
Start with W24x192, A= 56.3 in2, I = 6260 in4, ry = 3.07”, rx = 10.5”, Z = 559 in3

Assuming the weak axis for buckling governs	(to be check later)
Kl/r = (1 * 14' * 12”/ft) / 3.07” = 54.7
Fe = (π2 * 29,000) / (54.7)2 = 95.7 ksi >.44*(50 ksi)=22 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 50/95.7) * 50 = (0.6580.52247) * 50	= 40.18 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
0.9 * 40.18 ksi * 56.3 in2 = 2035.9k
    Check Required/Capacity	1094.1k/ 2035.9k = 0.537

Mu/ΦMn = (1119.3ft-k * 12”/ft) / (.9 * 559 in3 * 50ksi) = 0.534
(Not including P–Δ 0.537 + 0.534 = 1.07 > 1 Not OK! 1.07 * 192 #/ft = 205.6 #/ft

Try W24x229, A= 67.2 in2, I = 7650 in4, ry = 3.11”, rx = 10.7”, Z = 675 in3
Kl/r = (1 * 14' * 12”/ft) / 3.11” = 54.0
Fe = (π2 * 29,000)/(54.0)2 = 98.1 ksi > .44*(50 ksi)=22 ksi STILL INELASTIC CAN NOT USE EULER
Fcr = (0.658 ^50/98.1) * 50 = (0.6580.5096) * 50	= 40.39 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
0.9 * 40.39 ksi * 67.2 in2 = 2443.1k
    Check Required/Capacity	1094.1k/ 2443.1k = 0.448

Mu/ΦMn = (1119.3ft-k * 12”/ft) / (.9 * 675 in3 * 50ksi) = 0.442
(Not including P–Δ 0.448 + 0.442 = 0.89 < 1 OK!

For Preliminary Design from Base to Splice 2 use W24x229, A= 67.2 in2, I = 7650 in4, ry = 3.11”, rx = 10.7”, Z = 675 in3
Splice #2 to Splice #1 (L2 – L3)

ML2 – L3 Columns = 857.5ft-k ;
Forces at Splice #2 due to Wind = [W1 * (distance from Splice #2 to Level 3 + Level 4) + (W2 * distance from Splice #2 to Level 5) + (W3 * distance from Splice #2 to Level 6) ] / distance between rigid frame columns
    = [74.8k * (7' + 21') + (72.8k * 35') + (22.6k * 49')] / 24'
    = [ 2094.4ft-k + 2548.0ft-k + 1107.4ft-k ] / 24' = 239.6k (due to 1.6W)

PDown = 2P1 + P2 + P3 + Axial force from wind overturning
PDown = 2(142.56k) + 129.0k + 41.7k + 239.6k = 695.4k
(Note: Pmin = .9PDown = 625.9k> 239.6k therefore No Uplift)

At this point assuming Mn = Mprelim
Using this Moment only Zrequired = (857.5ft-k * 12”/ft) / (.9 * 50ksi) = 228.7 in3

Start with W24x146, A= 43.0 in2, I = 4580 in4, ry = 3.01”, rx = 10.3”, Z = 418 in3
Assuming the weak axis for buckling governs	(to be check later)
Kl/r = (1 * 14' * 12”/ft) / 3.01” = 55.8
Fe = (π2 * 29,000) / (55.8)2 = 91.9 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 50/91.9) * 50 = (0.6580.54407) * 50	= 39.82 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
0.9 * 39.82 ksi * 43.0 in2 = 1541.0k
    Check Required/Capacity	695.4k/ 1541.0k = 0.451

Mu/ΦMn = (857.5ft-k * 12”/ft) / (.9 * 418 in3 * 50ksi) = 0.547
(Not including P–Δ 0.451 + 0.442 = 0.998 < 1 OK!

For Preliminary Design from Splice #2 to Splice #1 use W24x146, A= 43.0 in2, I = 4580 in4, ry = 3.01”, rx = 10.3”, Z = 418 in3

Splice #1 to Top (L4 – L5)

ML4 – L5 Columns = 333.9ft-k ;
Forces at Splice #1 due to Wind = [(W2 * distance from Splice #1 to Level 5) + (W3 * distance from Splice #1 to Level 6) ] / distance between rigid frame columns
    = [(72.8k * 7') + (22.6k * 19')] / 24'
    = [ 551.6ft-k + 429.4ft-k ] / 24' = 40.9k (due to 1.6W)

PDown = P2 + P3 + Axial force from wind overturning
PDown = 129.0k + 41.7k + 40.9k = 211.6k
(Note: Pmin = .9PDown = 190.44k> 40.9k therefore No Uplift)

At this point assuming Mn = Mprelim
Using this Moment only Zrequired = (333.9ft-k * 12”/ft) / (.9 * 50ksi) = 89.04 in3

Start with W24x76, A= 22.4 in2, I = 2100 in4, ry = 1.92”, rx = 9.69”, Z = 200 in3
Assuming the weak axis for buckling governs	(to be check later)
Kl/r = (1 * 14' * 12”/ft) / 1.92” = 87.5
Fe = (π2 * 29,000) / (87.5)2 = 37.38 ksi > .44*(50 ksi)=22.0 ksi INELASTIC CAN NOT USE EULER
Fcr = (0.658 50/37.38) * 50 = (0.6581.3376) * 50	= 28.56 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
0.9 * 28.56 ksi * 22.4 in2 = 575.9k
    Check Required/Capacity	211.6k/ 575.9k = 0.367

Mu/ΦMn = (333.9ft-k * 12”/ft) / (.9 * 200 in3 * 50ksi) = 0.445
(Not including P–Δ 0.367 + 0.445 = 0.812 < 1 OK!

For Preliminary Design from Splice #1 to Top use W24x76, A= 22.4 in2, I = 2100 in4, ry = 1.92”, rx = 9.69”, Z = 200 in3

Summary of Preliminary Design for computer model :
Computer Model – 18 nodes (joints), 25 members, 15 nodes loaded, none pin ended.

Test the following use of beams and columns in the PLFNL2 program.

L6 Zrequired use	W14x68, Z=115 in3, A= 20.0 in2 , I= 722 in4
L5 Zrequired use	W21x83, Z=196 in3, A= 24.3 in2, I=1830 in4
L4 Zrequired use	W21x132, Z=333 in3, A= 38.8 in2, I=3220 in4
L3 Zrequired use	W30x148, Z=500 in3, A= 43.5 in2, I=6680 in4
L2 Zrequired use	W30x191, Z=675 in3, A= 56.3 in2, I=9200 in4
Splice #1 to top –	W24x76, Z = 200 in3, A= 22.4 in2, I = 2100 in4
Splice #2 to Splice #1 --W24x146, Z = 418 in3, A=43.0 in2, I = 4580 in4
Base to Splice #1 –	W24x229, Z = 675 in3, A= 67.2 in2, I = 7650 in4

In addition to the strength requirements limit the L6 lateral movement to height/150 due to factored loads, including P–Δ, 816” / 150 = 5.44” Computer model calculated 4.77” on Joints 6, 12, & 18 O.K.

PLFNL2 OUTPUT:

        NUMBER OF JOINTS = 18
        NUMBER OF MEMBERS = 25
        NUMBER OF JOINTS WITH APPLIED LOAD(S) = 15
        MODULUS OF ELASTICITY = 0.290E+05
        NUMBER OF PIN END MEMBERS = 0 ( -1 INDICATES TRUSS)
        NPD= 1(1 MEANS CALCULATE P-DELTA EFFECTS)

        SPRING CONSTANTS
 JOINT X Y SX SY SRZ

     1 0.0000E+00 0.0000E+00 0.100E+31 0.100E+31 0.100E+31
     2 0.0000E+00 0.1680E+03 0.000E+00 0.000E+00 0.000E+00
     3 0.0000E+00 0.3360E+03 0.000E+00 0.000E+00 0.000E+00
     4 0.0000E+00 0.5040E+03 0.000E+00 0.000E+00 0.000E+00
     5 0.0000E+00 0.6720E+03 0.000E+00 0.000E+00 0.000E+00
     6 0.0000E+00 0.8160E+03 0.000E+00 0.000E+00 0.000E+00
     7 0.2880E+03 0.0000E+00 0.100E+31 0.100E+31 0.100E+31
     8 0.2880E+03 0.1680E+03 0.000E+00 0.000E+00 0.000E+00
     9 0.2880E+03 0.3360E+03 0.000E+00 0.000E+00 0.000E+00
    10 0.2880E+03 0.5040E+03 0.000E+00 0.000E+00 0.000E+00
    11 0.2880E+03 0.6720E+03 0.000E+00 0.000E+00 0.000E+00
    12 0.2880E+03 0.8160E+03 0.000E+00 0.000E+00 0.000E+00
    13 0.4000E+03 0.0000E+00 0.100E+31 0.100E+31 0.000E+00
    14 0.4000E+03 0.1680E+03 0.000E+00 0.000E+00 0.000E+00
    15 0.4000E+03 0.3360E+03 0.000E+00 0.000E+00 0.000E+00
    16 0.4000E+03 0.5040E+03 0.000E+00 0.000E+00 0.000E+00
    17 0.4000E+03 0.6720E+03 0.000E+00 0.000E+00 0.000E+00
    18 0.4000E+03 0.8160E+03 0.000E+00 0.000E+00 0.000E+00

     MEMBER J NODE K NODE AREA INERTIA
        1 1 2 0.672E+02 0.765E+04
        2 2 3 0.430E+02 0.458E+04
        3 3 4 0.430E+02 0.458E+04
        4 4 5 0.224E+02 0.210E+04
        5 5 6 0.224E+02 0.210E+04
        6 7 8 0.672E+02 0.765E+04
        7 8 9 0.430E+02 0.458E+04
        8 9 10 0.430E+02 0.458E+04
        9 10 11 0.224E+02 0.210E+04
        10 11 12 0.224E+02 0.210E+04
        11 2 8 0.563E+02 0.920E+04
        12 3 9 0.435E+02 0.668E+04
        13 4 10 0.388E+02 0.322E+04
        14 5 11 0.243E+02 0.183E+04
        15 6 12 0.200E+02 0.722E+03
        16 13 14 -0.100E+03 0.100E+01
        17 14 15 -0.100E+03 0.100E+01
        18 15 16 -0.100E+03 0.100E+01
        19 16 17 -0.100E+03 0.100E+01
        20 17 18 -0.100E+03 0.100E+01
        21 8 14 -0.100E+03 0.100E+01
        22 9 15 -0.100E+03 0.100E+01
        23 10 16 -0.100E+03 0.100E+01
        24 11 17 -0.100E+03 0.100E+01
        25 12 18 -0.100E+03 0.100E+01

     MEMBER LOADS
  MEMBER W AT J W AT K P1 D1 P2 D2 P3 D3

     JOINT XFORCE YFORCE ZMOM

        2 0.748E+02 -0.143E+03 0.000E+00
        3 0.748E+02 -0.143E+03 0.000E+00
        4 0.748E+02 -0.143E+03 0.000E+00
        5 0.728E+02 -0.129E+03 0.000E+00
        6 0.226E+02 -0.417E+02 0.000E+00
        8 0.000E+00 -0.143E+03 0.000E+00
        9 0.000E+00 -0.143E+03 0.000E+00
        10 0.000E+00 -0.143E+03 0.000E+00
        11 0.000E+00 -0.129E+03 0.000E+00
        12 0.000E+00 -0.417E+02 0.000E+00
        14 0.000E+00 -0.983E+03 0.000E+00
        15 0.000E+00 -0.983E+03 0.000E+00
        16 0.000E+00 -0.983E+03 0.000E+00
        17 0.000E+00 -0.820E+03 0.000E+00
        18 0.000E+00 -0.147E+03 0.000E+00

     OUTPUT NOT INCLUDING P-DELTA EFFECTS

        JOINT DISPLACEMENTS AND REACTIONS

     JT X DISPL Y DISPL Z ROT X REACT Y REACT ZM REACT
     1 0.161D-27 -0.232D-27 -0.185D-25 -0.161E+03 0.232E+03 0.185E+05
     2 0.602D+00 -0.200D-01 -0.376D-02 0.000E+00 0.000E+00 0.000E+00
     3 0.168D+01 -0.502D-01 -0.475D-02 0.000E+00 0.000E+00 0.000E+00
     4 0.281D+01 -0.775D-01 -0.572D-02 0.000E+00 0.000E+00 0.000E+00
     5 0.401D+01 -0.111D+00 -0.481D-02 0.000E+00 0.000E+00 0.000E+00
     6 0.466D+01 -0.118D+00 -0.360D-02 0.000E+00 0.000E+00 0.000E+00
     7 0.159D-27 -0.967D-27 -0.183D-25 -0.159E+03 0.967E+03 0.183E+05
     8 0.596D+00 -0.834D-01 -0.372D-02 0.000E+00 0.000E+00 0.000E+00
     9 0.167D+01 -0.176D+00 -0.475D-02 0.000E+00 0.000E+00 0.000E+00
    10 0.280D+01 -0.233D+00 -0.570D-02 0.000E+00 0.000E+00 0.000E+00
    11 0.400D+01 -0.288D+00 -0.482D-02 0.000E+00 0.000E+00 0.000E+00
    12 0.465D+01 -0.299D+00 -0.368D-02 0.000E+00 0.000E+00 0.000E+00
    13 0.145D-32 -0.392D-26 -0.378D-02 -0.145E-02 0.392E+04 0.000E+00
    14 0.596D+00 -0.227D+00 -0.308D-02 0.000E+00 0.000E+00 0.000E+00
    15 0.167D+01 -0.397D+00 -0.473D-02 0.000E+00 0.000E+00 0.000E+00
    16 0.280D+01 -0.510D+00 -0.498D-02 0.000E+00 0.000E+00 0.000E+00
    17 0.400D+01 -0.566D+00 -0.446D-02 0.000E+00 0.000E+00 0.000E+00
    18 0.465D+01 -0.573D+00 -0.306D-02 0.000E+00 0.000E+00 0.000E+00

        MEMBER END ACTIONS

 MEMBER J K AX J SHR J MOM J AX K SHR K MOM K
   1 1 2 0.232E+03 0.161E+03 0.185E+05 -0.232E+03 -0.161E+03 0.855E+04
   2 2 3 0.225E+03 0.122E+03 0.111E+05 -0.225E+03 -0.122E+03 0.949E+04
   3 3 4 0.202E+03 0.850E+02 0.791E+04 -0.202E+03 -0.850E+02 0.637E+04
   4 4 5 0.129E+03 0.480E+02 0.370E+04 -0.129E+03 -0.480E+02 0.436E+04
   5 5 6 0.326E+02 0.110E+02 0.278E+03 -0.326E+02 -0.110E+02 0.131E+04
   6 7 8 0.967E+03 0.159E+03 0.183E+05 -0.967E+03 -0.159E+03 0.843E+04
   7 8 9 0.689E+03 0.123E+03 0.111E+05 -0.689E+03 -0.123E+03 0.949E+04
   8 9 10 0.425E+03 0.852E+02 0.791E+04 -0.425E+03 -0.852E+02 0.640E+04
   9 10 11 0.212E+03 0.474E+02 0.366E+04 -0.212E+03 -0.474E+02 0.430E+04
  10 11 12 0.508E+02 0.116E+02 0.350E+03 -0.508E+02 -0.116E+02 0.132E+04
  11 2 8 0.363E+02 -0.136E+03 -0.196E+05 -0.363E+02 0.136E+03 -0.195E+05
  12 3 9 0.374E+02 -0.121E+03 -0.174E+05 -0.374E+02 0.121E+03 -0.174E+05
  13 4 10 0.378E+02 -0.699E+02 -0.101E+05 -0.378E+02 0.699E+02 -0.101E+05
  14 5 11 0.358E+02 -0.322E+02 -0.464E+04 -0.358E+02 0.322E+02 -0.465E+04
  15 6 12 0.116E+02 -0.911E+01 -0.131E+04 -0.116E+02 0.911E+01 -0.132E+04
  16 13 14 0.392E+04 0.145E-02 0.341E-15 -0.392E+04 -0.145E-02 0.244E+00
  17 14 15 0.293E+04 0.309E-01 0.288E+01 -0.293E+04 -0.309E-01 0.231E+01
  18 15 16 0.195E+04 0.232E-01 0.199E+01 -0.195E+04 -0.232E-01 0.190E+01
  19 16 17 0.967E+03 0.293E-01 0.237E+01 -0.967E+03 -0.293E-01 0.255E+01
  20 17 18 0.147E+03 0.138E-01 0.710E+00 -0.147E+03 -0.138E-01 0.127E+01
  21 8 14 -0.294E-01 -0.588E-01 -0.346E+01 0.294E-01 0.588E-01 -0.312E+01
  22 9 15 0.770E-02 -0.768E-01 -0.431E+01 -0.770E-02 0.768E-01 -0.430E+01
  23 10 16 -0.610E-02 -0.797E-01 -0.465E+01 0.610E-02 0.797E-01 -0.427E+01
  24 11 17 0.155E-01 -0.599E-01 -0.345E+01 -0.155E-01 0.599E-01 -0.326E+01
  25 12 18 0.138E-01 -0.256E-01 -0.159E+01 -0.138E-01 0.256E-01 -0.127E+01

        OUTPUT INCLUDING P-DELTA EFFECTS
     NUMBER OF CYCLES= 2

        JOINT DISPLACEMENTS AND REACTIONS

     JT X DISPL Y DISPL Z ROT X REACT Y REACT ZM REACT
     1 0.162D-27 -0.223D-27 -0.188D-25 -0.162E+03 0.223E+03 0.188E+05
     2 0.613D+00 -0.192D-01 -0.384D-02 0.000E+00 0.000E+00 0.000E+00
     3 0.172D+01 -0.487D-01 -0.487D-02 0.000E+00 0.000E+00 0.000E+00
     4 0.288D+01 -0.756D-01 -0.587D-02 0.000E+00 0.000E+00 0.000E+00
     5 0.411D+01 -0.109D+00 -0.493D-02 0.000E+00 0.000E+00 0.000E+00
     6 0.477D+01 -0.116D+00 -0.368D-02 0.000E+00 0.000E+00 0.000E+00
     7 0.157D-27 -0.976D-27 -0.185D-25 -0.157E+03 0.976E+03 0.185E+05
     8 0.607D+00 -0.841D-01 -0.380D-02 0.000E+00 0.000E+00 0.000E+00
     9 0.171D+01 -0.178D+00 -0.486D-02 0.000E+00 0.000E+00 0.000E+00
    10 0.287D+01 -0.235D+00 -0.585D-02 0.000E+00 0.000E+00 0.000E+00
    11 0.409D+01 -0.290D+00 -0.494D-02 0.000E+00 0.000E+00 0.000E+00
    12 0.477D+01 -0.302D+00 -0.376D-02 0.000E+00 0.000E+00 0.000E+00
    13 0.149D-32 -0.392D-26 -0.385D-02 -0.149E-02 0.392E+04 0.000E+00
    14 0.607D+00 -0.227D+00 -0.313D-02 0.000E+00 0.000E+00 0.000E+00
    15 0.171D+01 -0.397D+00 -0.482D-02 0.000E+00 0.000E+00 0.000E+00
    16 0.287D+01 -0.510D+00 -0.506D-02 0.000E+00 0.000E+00 0.000E+00
    17 0.409D+01 -0.566D+00 -0.453D-02 0.000E+00 0.000E+00 0.000E+00
    18 0.477D+01 -0.573D+00 -0.307D-02 0.000E+00 0.000E+00 0.000E+00

        MEMBER END ACTIONS

 MEMBER J K AX J SHR J MOM J AX K SHR K MOM K
   1 1 2 0.223E+03 0.162E+03 0.188E+05 -0.223E+03 -0.162E+03 0.865E+04
   2 2 3 0.219E+03 0.124E+03 0.113E+05 -0.219E+03 -0.124E+03 0.972E+04
   3 3 4 0.200E+03 0.858E+02 0.811E+04 -0.200E+03 -0.858E+02 0.653E+04
   4 4 5 0.128E+03 0.483E+02 0.380E+04 -0.128E+03 -0.483E+02 0.448E+04
   5 5 6 0.324E+02 0.110E+02 0.277E+03 -0.324E+02 -0.110E+02 0.133E+04
   6 7 8 0.976E+03 0.157E+03 0.185E+05 -0.976E+03 -0.157E+03 0.855E+04
   7 8 9 0.694E+03 0.121E+03 0.114E+05 -0.694E+03 -0.121E+03 0.972E+04
   8 9 10 0.428E+03 0.844E+02 0.811E+04 -0.428E+03 -0.844E+02 0.656E+04
   9 10 11 0.213E+03 0.471E+02 0.375E+04 -0.213E+03 -0.471E+02 0.441E+04
  10 11 12 0.510E+02 0.115E+02 0.350E+03 -0.510E+02 -0.115E+02 0.135E+04
  11 2 8 0.364E+02 -0.139E+03 -0.200E+05 -0.364E+02 0.139E+03 -0.199E+05
  12 3 9 0.367E+02 -0.124E+03 -0.178E+05 -0.367E+02 0.124E+03 -0.178E+05
  13 4 10 0.374E+02 -0.717E+02 -0.103E+05 -0.374E+02 0.717E+02 -0.103E+05
  14 5 11 0.355E+02 -0.330E+02 -0.475E+04 -0.355E+02 0.330E+02 -0.476E+04
  15 6 12 0.116E+02 -0.931E+01 -0.133E+04 -0.116E+02 0.931E+01 -0.135E+04
  16 13 14 0.392E+04 0.149E-02 0.274E-15 -0.392E+04 -0.149E-02 0.251E+00
  17 14 15 0.293E+04 0.319E-01 0.297E+01 -0.293E+04 -0.319E-01 0.239E+01
  18 15 16 0.195E+04 0.242E-01 0.208E+01 -0.195E+04 -0.242E-01 0.199E+01
  19 16 17 0.967E+03 0.306E-01 0.247E+01 -0.967E+03 -0.306E-01 0.266E+01
  20 17 18 0.147E+03 0.148E-01 0.772E+00 -0.147E+03 -0.148E-01 0.136E+01
  21 8 14 -0.304E-01 -0.607E-01 -0.357E+01 0.304E-01 0.607E-01 -0.323E+01
  22 9 15 0.769E-02 -0.800E-01 -0.449E+01 -0.769E-02 0.800E-01 -0.447E+01
  23 10 16 -0.631E-02 -0.834E-01 -0.488E+01 0.631E-02 0.834E-01 -0.447E+01
  24 11 17 0.157E-01 -0.632E-01 -0.364E+01 -0.157E-01 0.632E-01 -0.343E+01
  25 12 18 0.148E-01 -0.275E-01 -0.172E+01 -0.148E-01 0.275E-01 -0.136E+01

Verify Preliminary Design using PLFNL2 P–Δ Output
Beam L6 (Member 15), W14x68, Z=115 in3, A= 20.0 in2 , I= 722 in4 , d=14.0”, tw= 0.415”
Axial Force – 11.6k © σ = P/A = 11.6/20 = 0.58 ksi negligible
Shear – 9.31k ; Check shear: LRFD (d * tw * ksi) > Vmax
14” * 0.415” * 50 ksi = 290.5k > 9.31k	Shear O.K.
Max Moment – 1350in-k = 112.5ft-k
ΦcZFy= .9 * 115 in3 * 50ksi = 5175in-k > 1350in-k	Moment O.K.

Beam L5 (Member 14), W21x83, Z=196 in3, A= 24.3 in2, I=1830 in4, d=21.4”, tw= 0.515”
Axial Force – 35.5k © σ = P/A = 35.5/ 24.3 = 1.46 ksi negligible
Shear – 33k ; Check shear: LRFD (d * tw * ksi) > Vmax
21.4” * 0.515” * 50 ksi = 551.0k > 33k	Shear O.K.
Max Moment – 4760in-k = 396.7ft-k
        ΦcZFy= .9 * 196 in3 * 50ksi = 8820in-k > 4760in-k	Moment O.K.

Beam L4 (Member 13), W21x132, Z=333 in3, A= 38.8 in2, I=3220 in4, d=21.8”, tw= 0.650”
Axial Force – 37.4k © σ = P/A = 37.4/ 38.8 = 0.96 ksi negligible
Shear – 71.7k ; Check shear: LRFD (d * tw * ksi) > Vmax
21.8” * 0.650” * 50 ksi = 708.6k > 71.7k	Shear O.K.
Max Moment – 10,300in-k = 858.3ft-k
        ΦcZFy= .9 * 333 in3 * 50ksi = 14,985in-k > 10,300in-k Moment O.K.

Beam L3 (Member 12), W30x148, Z=500 in3, A= 43.5 in2, I=6680 in4, d=30.7”, tw= 0.650”
Axial Force – 36.7k © σ = P/A = 36.7/ 43.5 = 0.84 ksi negligible
Shear – 124.0k ; Check shear: LRFD (d * tw * ksi) > Vmax
30.7” * 0.650” * 50 ksi = 997.7k > 124k	Shear O.K.
Max Moment – 17,800in-k = 1,483.3ft-k
        ΦcZFy= .9 * 500 in3 * 50ksi = 22,500in-k > 17,800in-k	Moment O.K.

Beam L2 (Member 11), W30x191, Z=675 in3, A= 56.3 in2, I=9200 in4, d=30.7”, tw= 0.710”
Axial Force – 36.4k © σ = P/A = 36.4/ 56.3 = 0.65 ksi negligible
Shear – 139.0k ; Check shear: LRFD (d * tw * ksi) > Vmax
30.7” * 0.710” * 50 ksi = 1089.8k > 139k	Shear O.K.
Max Moment – 20,000in-k = 1,483.3ft-k
        ΦcZFy= .9 * 675 in3 * 50ksi = 30,375in-k > 20,000in-k	Moment O.K.

NOTE: Even though these calculations are substantially larger than required they actually support the lateral deflection @ 4.77” < 5.44” max

Verify Preliminary Column Design
Column Top to Splice #1(Members 4, 5, 9, 10); W24x76, Z = 200 in3, A= 22.4 in2, Iin plane = 2100 in4, d=23.9”, tw= 0.440”, rin plane = 9.69”, rout plane = 1.92”
Pu = Axial Force = 213k © σ = P/A = 213/ 22.4 = 9.51 ksi
Shear = 48.3k ; Check shear: LRFD (d * tw * ksi) > Vmax
22.4” * 0.440” * 50 ksi = 492.8k > 48.3k	Shear O.K.
Mu = Max Moment = 4,480in-k = 373.3ft-k
        ΦcZFy= .9 * 200 in3 * 50ksi = 9,000in-k > 4,480in-k	Moment O.K.

Leaning Column Factor at L4 to L5
= 2(P2 + P3) + P6 + P5 = 2(129k + 41.7k) + 146.5k + 819.5k = 341.4k + 966.0k) = 3.83k
        2(P2 + P3)	2(129k + 41.7k)	341.4k
GIRDER B = Σ E I/L column /Σ E I/L beam = [2100/12 + 2100/14] / [1830/24]= 2.95
GIRDER C = Σ E I/L column /Σ E I/L beam = [2100/14 + 4580/14] / [3220/24]= 3.56

From Sidesway uninhibited nomograph, (AISC 16.1 – 242): K= 1.9
K'inplane = K * √N = 1.9 * √3.83 = 3.7
Kl/r out-of-plane = (1.0 * 14' * 12”/1') / 1.92” = 87.5	governs
K'l/r in-plane = (3.7 * 14' * 12”/1') / 9.69” = 64.1
Fe = (π2 * 29,000) / (87.5)2 = 37.38 ksi > .44*(50 ksi)=22 ksi	IN-ELASTIC
Fcr = (0.658 50/37.38) * 50 = (0.6581.3376) * 50	= 28.56 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
 0.9 * 28.56 ksi * 22.4 in2 = 575.9k
  Pu/ΦPn = 213k © / 575.9k = 0.370 > 0.20
Lb = 14',	Lp = 1.76 * rout plane * √E/Fy = 1.76 * 1.92 * √(29,000/50) = 81.38” (6.78')
AISC 16.1-46
= (12.5 * 4410) / ((2.5*4410) + (3*2370) + (4*330) + (3*3750))
= 55125/30705 = 1.79 < 3.0
 (From Tbl 3-2) W24x76 = BFLRFD = 22.5k, ΦMp = 750ft-k Lp = 6.78' (81.36”)
ΦMn = Cb[ΦMp – BFLRFD * (Lb – Lp)] < ΦMp
  = 1.79[750ft-k – 22.5k(14' – 6.78')] = 1.79 * (587.55ft-k) = 1054.7 > 750ft-k ; therefore ΦMn = ΦMp =750ft-k
Pu/ΦPn + (8/9) * (Mu/ΦMn) = 0.370 + (8/9) * ( 373.3ft-k/ 750ft-k) = 0.370 + 0.4424 = 0.8124 < 1 O.K.

Use W24x76 for top section of columns in rigid frame

Column Splice #1 to Splice #2 (Members 2, 3, 7, 8); W24x146, Z = 418 in3, A=43.0 in2, I = 4580 in4, d=24.7”, tw= 0.650”, rin plane = 10.3”, rout plane = 3.01”
Pu = Axial Force = 694k © σ = P/A = 694/43 = 16.1 ksi
Shear = 124k ; Check shear: LRFD (d * tw * ksi) > Vmax
24.7” * 0.650” * 50 ksi = 802.8k > 124k	Shear O.K.
Mu = Max Moment = 11,400in-k = 950ft-k
        ΦcZFy= .9 * 418 in3 * 50ksi = 18,810in-k > 4,480in-k	Moment O.K.
Leaning Column Factor at L2 to L3
= 2[(P2 + P3) + 3(P1)] + P6 + P5 + 3(P4) = 2[(129k + 41.7k) + 3(143k)] + 146.5k + 819.5k + 3(983k) =
        2[(P2 + P3) + 3(P1)]	2[(129k + 41.7k) + 3(143k)]
 2[599.7k] + 3915.0k = 5114.4k = 4.26k
        2[599.7k]	1199.4k

GIRDER D = Σ E I/L column /Σ E I/L beam = [4580/14 + 4580/14] / [6680/24]= 2.35
GIRDER E = Σ E I/L column /Σ E I/L beam = [4580/14 + 7650/14] / [9200/24]= 2.28
From Sidesway uninhibited nomograph, (AISC 16.1 – 242): K= 1.7
K'inplane = K * √N = 1.7 * √4.26 = 3.51
Kl/r out-of-plane = (1.0 * 14' * 12”/1') / 3.01” = 55.8
K'l/r in-plane = (3.51 * 14' * 12”/1') / 10.3” = 57.2	governs
Fe = (π2 * 29,000) / (57.2)2 = 87.48 > .44 * (50 ksi)=22 ksi	IN-ELASTIC
Fcr = (0.658 50/87.48) * 50 = (0.6580.57156) * 50	= 39.36 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
 0.9 * 39.36 ksi * 43.0 in2 = 1523.3k
  Pu/ΦPn = 694k © / 1523.3k = 0.4556 > 0.20
Lb = 14',	Lp = 1.76 * rout plane * √E/Fy = 1.76 * 3.01 * √(29,000/50) = 127.58” (10.62')
AISC 16.1-46
= (12.5 * 11,400) / ((2.5*11,400) + (3*4440) + (4*840) + (3*6120))
= 142,500/63,540 = 2.24 < 3.0

 (From Tbl 3-2) W24x146 = BFLRFD = 25.8k, ΦMp = 1570ft-k Lp = 10.6' (127.2”)
ΦMn = Cb[ΦMp – BFLRFD * (Lb – Lp)] < ΦMp
        = Cb [1570ft-k – 25.8k(14' – 10.6')] = 2.24 * (1482.28ft-k) = 3324 > 1570ft-k ; therefore ΦMn = ΦMp = 1570ft-k
Pu/ΦPn + (8/9) * (Mu/ΦMn) = 0. 494 + (8/9) * ( 950ft-k/ 1570ft-k) = 0.4556 + 0.5379 = 0.9935 < 1 O.K.

Use W24x146 for middle section of columns in rigid frame

Column Splice #2 to Base (Members 1, 6); W24x229, Z = 675 in3, A= 67.2 in2, I = 7650 in4, d=26.0”, tw= 0.960”, rin plane = 10.7”, rout plane = 3.11”
Pu = Axial Force = 976k © σ = P/A = 976/67.2 = 14.5 ksi
Shear = 162k ; Check shear: LRFD (d * tw * ksi) > Vmax
26.0” * 0.960” * 50 ksi = 1248k > 162k	Shear O.K.
Mu = Max Moment = 18,800in-k = 1,566.7ft-k
        ΦcZFy= .9 * 675 in3 * 50ksi = 30,375in-k > 18,800in-k	Moment O.K.

Fcr = (0.658 50/65.51) * 50 = (0.6580.7632) * 50	= 36.33 ksi

LRFD Φc=0.90
Φc x Pn	(Pn = Fcr x Ag)
 0.9 * 36.33 ksi * 67.2 in2 = 2197.2k
  Pu/ΦPn = 976k © / 2197.2k = 0.444 > 0.20
Lb = 14',	Lp = 1.76 * rout plane * √E/Fy = 1.76 * 3.11 * √(29,000/50) = 131.8” (10.98')
AISC 16.1-46

= (12.5 * 18,800) / ((2.5*18,800) + (3*1787) + (4*5075) + (3*11937))
= 235,000/108472 = 2.17 < 3.0
 (From Tbl 3-2) W24x229 = BFLRFD = 28.9k, ΦMp = 2530ft-k Lp = 11.0'
ΦMn = Cb[ΦMp – BFLRFD * (Lb – Lp)] < ΦMp
        = 2.17 [2530ft-k – 28.9k(14' – 11')] = 2.17*(2443.3ft-k) = 5293 > 2530ft-k ; therefore ΦMn = ΦMp = 2530ft-k
Pu/ΦPn + (8/9) * (Mu/ΦMn) = 0. 444 + (8/9) * ( 1567ft-k/ 2530ft-k) = 0.444 + 0.551 = 0.9945 < 1 O.K.

Use W24x229 for bottom section of columns in rigid frame