Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications


Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 02221 - BUILDING DEMOLITION
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project

1. Demolition and removal of buildings and site improvements.

2. Abandoning in place and removing below-grade construction.

3. Disconnecting, capping or sealing, and abandoning in-place an removing site utilities.

4. Salvaging items for reuse by Owner.

1.2 DEFINITIONS

Retain definitions and terms that remain after this Section has been edited.

A. Demolish:  Completely remove and legally dispose of off-site.

B. Recycle:  Recovery of demolition waste for subsequent processing in preparation for reuse.

C. Salvage:  Carefully detach from existing construction, in a manner to prevent damage, and deliver to Owner.  Include fasteners or brackets needed for reattachment elsewhere.

1.3 MATERIALS OWNERSHIP

A. Unless otherwise indicated, demolition waste becomes property of Contractor.

B. Historic items, relics, antiques, and similar objects including, but not limited to, cornerstones and their contents, commemorative plaques and tablets, and other items of interest or value to Owner that may be uncovered during demolition remain the property of Owner.

1. Carefully salvage in a manner to prevent damage and promptly return to Owner.

1.4 SUBMITTALS

A. Qualification Data:  For refrigerant recovery technician.

B. Proposed Protection Measures:  Submit informational report, including drawings, that indicates the measures proposed for protecting individuals and property, for environmental protection, for dust control and, for noise control.  Indicate proposed locations and construction of barriers.

1. Adjacent Buildings:  Detail special measures proposed to protect adjacent buildings to remain.

C. Schedule of Building Demolition Activities:  Indicate the following:

1. Detailed sequence of demolition work, with starting and ending dates for each activity.

2. Temporary interruption of utility services.

3. Shutoff and capping or re-routing of utility services.

D. Building Demolition Plans:  Drawings indicating the following:

1. Locations of temporary protection.

E. Inventory:  Submit a list of items to be removed and salvaged and deliver to Owner prior to start of demolition.

F. Predemolition Photographs or Video:  Show existing conditions of adjoining construction and site improvements, including finish surfaces, that might be misconstrued as damage caused by building demolition operations.  Comply with Division 01 Section "Photographic Documentation." Submit before the Work begins.

Retain record submittal in first paragraph below if applicable.  Landfill records may be required by Owner when demolished materials contain hazardous wastes or, in rare circumstances, where recycling is not allowed.

G. Landfill Records:  Indicate receipt and acceptance of hazardous wastes by a landfill facility licensed to accept hazardous wastes.

H. Statement of Refrigerant Recovery:  Signed by refrigerant recovery technician responsible for recovering refrigerant, stating that all refrigerant that was present was recovered and that recovery was performed according to EPA regulations.  Include name and address of technician and date refrigerant was recovered.

1.5 QUALITY ASSURANCE

A. Refrigerant Recovery Technician Qualifications:  Certified by EPA-approved certification program.

B. Regulatory Requirements:  Comply with governing EPA notification regulations before beginning demolition.  Comply with hauling and disposal regulations of authorities having jurisdiction.

C. Standards:  Comply with ANSI A10.6 and NFPA 241.

D. Predemolition Conference:  Conduct conference at Project site to comply with requirements in Division 01 Section "Project Management and Coordination."

1.6 PROJECT CONDITIONS

A. Buildings to be demolished will be vacated and their use discontinued before start of the Work.

B. Buildings immediately adjacent to demolition area will be occupied.  Conduct building demolition so operations of occupied buildings will not be disrupted.

1. Provide not less than 72 hours' notice of activities that will affect operations of adjacent occupied buildings.

2. Maintain access to existing walkways, exits, and other facilities used by occupants of adjacent buildings.

a. Do not close or obstruct walkways, exits, or other facilities used by occupants of adjacent buildings without written permission from authorities having jurisdiction.

C. Owner assumes no responsibility for buildings and structures to be demolished.

1. Conditions existing at time of inspection for bidding purpose will be maintained by Owner as far as practical.

Retain one of first two paragraphs and associated subparagraphs below, or remove all references to hazardous materials.  Expand scope of Article to include asbestos, PCBs, and other materials if required.  Coordinate statements with the General and Supplementary Conditions.  See Evaluations.

D. Hazardous Materials:  It is not expected that hazardous materials will be encountered in the Work.

Retain subparagraph below to cover instances where hazardous materials are unexpectedly found and must be remediated.  See the General Conditions for additional requirements on hazardous materials.

1. If materials suspected of containing hazardous materials are encountered, do not disturb; immediately notify Architect and Owner.  Hazardous materials will be removed by Owner under a separate contract.

Retain first paragraph and subparagraphs below if hazardous material remediation is part of the Work of this Contract.  Consult a professional liability insurance carrier for current recommendations.  Indemnification and a waiver of claims may be required from Owner as a condition for providing services related to hazardous material remediation.

E. On-site storage or sale of removed items or materials is not permitted.

1.7 COORDINATION

A. Arrange demolition schedule so as not to interfere with LAARNG's on-site operations and operations of adjacent occupied buildings.

PART 2 -  PRODUCTS

Delete "(Not Used)" option in Part 2 title above if retaining "Soil Materials" Article for backfilling voids that result from demolition operations in below-grade areas.  Coordinate with requirements in Part 3.

2.1 SOIL MATERIALS

A. Satisfactory Soils:  Comply with requirements in Division 2 Section "Earthwork."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Verify that utilities have been disconnected and capped before starting demolition operations.

B. Review Project Record Documents of existing construction provided by LAARNG.  LAARNG does not guarantee that existing conditions are same as those indicated in Project Record Documents.

C. Inventory and record the condition of items to be removed and salvaged.

Usually retain first option in paragraph below.  OSHA regulations require that a "competent person" perform an engineering survey before building demolition begins.

D. Perform an engineering survey of condition of building to determine whether removing any element might result in structural deficiency or unplanned collapse of any portion of structure or adjacent structures during building demolition operations.

Retain subparagraph below if demolition includes prestressed or post-tensioned concrete slabs.

1. Steel Tendons:  Locate tensioned steel tendons and include recommendations for de-tensioning.

Retain paragraph below if hazardous material remediation is part of the Work of this Contract.

E. Verify that hazardous materials have been remediated before proceeding with building demolition operations.

3.2 PREPARATION

A. Refrigerant:  Remove refrigerant from mechanical equipment according to 40 CFR 82 and regulations of authorities having jurisdiction before starting demolition.

Retain one of two "Existing Utilities" paragraphs below if applicable.

B. Existing Utilities:  Locate, identify, disconnect, and seal or cap off indicated utilities serving buildings and structures to be demolished.

Retain subparagraph below if shutting off utilities is responsibility of Owner.  Delete if it is responsibility of Contractor.

Retain first subparagraph below if shutting off utilities is responsibility of Contractor.  Delete if it is responsibility of Owner.

1. Arrange to shut off indicated utilities with utility companies.

2. If removal, relocation, or abandonment of utility services will affect adjacent occupied buildings, then provide temporary utilities that bypass buildings and structures to be demolished and that maintain continuity of service to other buildings and structures.

3. Cut off pipe or conduit a minimum of 24 inches (610 mm) below grade.  Cap, valve, or plug and seal remaining portion of pipe or conduit after bypassing according to requirements of authorities having jurisdiction.

C. Temporary Shoring:  Provide and maintain interior and exterior shoring, bracing, or structural support to preserve stability and prevent unexpected movement or collapse of construction being demolished.

1. Strengthen or add new supports when required during progress of demolition.

D. Salvaged Items:  Comply with the following:

1. Clean salvaged items of dirt and demolition debris.

2. Pack or crate items after cleaning.  Identify contents of containers.

3. Store items in a secure area until delivery to LAARNG.

4. Transport items to storage area designated by LAARNG.

5. Protect items from damage during transport and storage.

3.3 PROTECTION

A. Existing Facilities:  Protect adjacent building facilities and site improvements during demolition operations.  Maintain exits from existing buildings.

B. Existing Utilities:  Maintain utility services to remain and protect from damage during demolition operations.

1. Do not interrupt existing utilities serving adjacent occupied or operating facilities unless authorized in writing by LAARNG and authorities having jurisdiction.

2. Provide temporary services during interruptions to existing utilities, as acceptable to LAARNG and authorities having jurisdiction.

a. Provide at least 72 hours' notice to occupants of affected buildings if shutdown of service is required during changeover.

C. Temporary Protection:  Erect temporary protection, such as walks, fences, railings, canopies, and covered passageways, where required by authorities having jurisdiction, and as indicated.  Comply with requirements in Division 01 Section "Temporary Facilities and Controls."

1. Protect adjacent buildings and facilities from damage due to demolition activities.

2. Protect existing site improvements, appurtenances, and landscaping to remain.

3. Provide temporary barricades and other protection required to prevent injury to people and damage to adjacent buildings and facilities to remain.

4. Provide protection to ensure safe passage of people around building demolition area and to and from occupied portions of adjacent buildings and structures.

5. Protect walls, windows, roofs, and other adjacent exterior construction that are to remain and that are exposed to building demolition operations.

D. Remove temporary barriers and protections where hazards no longer exist.  Where open excavations or other hazardous conditions remain, leave temporary barriers and protections in place.

3.4 DEMOLITION, GENERAL

A. General:  Demolish indicated existing buildings and site improvements completely.  Use methods required to complete the Work within limitations of governing regulations and as follows:

1. Do not use cutting torches until work area is cleared of flammable materials.  Maintain portable fire-suppression devices during flame-cutting operations.

2. Maintain fire watch during and after flame cutting operations.

3. Maintain adequate ventilation when using cutting torches.

4. Locate building demolition equipment and remove debris and materials so as not to impose excessive loads on supporting walls, floors, or framing.

Retain first paragraph below if engineers need to be on hand during the course of demolition work, for example, when prestressed tendons may be cut.  Revise to suit Project or delete.

B. Engineering Surveys:  During demolition, perform surveys to detect hazards that may result from building demolition activities.

C. Site Access and Temporary Controls:  Conduct building demolition and debris-removal operations to ensure minimum interference with roads, streets, walks, walkways, and other adjacent occupied and used facilities.

1. Do not close or obstruct streets, walks, walkways, or other adjacent occupied or used facilities without permission from LAARNG and authorities having jurisdiction.  Provide alternate routes around closed or obstructed traffic ways if required by authorities having jurisdiction.

2. Use water mist and other suitable methods to limit spread of dust and dirt.  Comply with governing environmental-protection regulations.  Do not use water when it may damage adjacent construction or create hazardous or objectionable conditions, such as ice, flooding, and pollution.

D. Explosives:  Use of explosives is not permitted.

3.5 DEMOLITION BY MECHANICAL MEANS

A. Proceed with demolition of structural framing members systematically, from higher to lower level.  Complete building demolition operations above each floor or tier before disturbing supporting members on the next lower level.

B. Remove debris from elevated portions of the building by chute, hoist, or other device that will convey debris to grade level in a controlled descent.

1. Remove structural framing members and lower to ground by method suitable to minimize ground impact and dust generation.

C. Salvage:  Items to be salvaged are indicated on Drawings. 

Retain one of three "Below-Grade Construction" paragraphs and associated subparagraph below.  Coordinate with other Division 31 Sections.  Revise to suit Project.

D. Below-Grade Construction:  Demolish foundation and other below-grade construction.

1. Remove below-grade construction, including foundations, and footings, completely.

Retain one of three "Existing Utilities" paragraphs and associated subparagraph below.  Coordinate with other Division 31 Sections.  Revise to suit Project.

E. Existing Utilities:  Demolish and remove existing utilities and below-grade utility structures.

3.6 SITE RESTORATION

Retain one of first two paragraphs below; coordinate with Division 31 Section "Earth Moving."

A. Below-Grade Areas:  Rough grade below-grade areas ready for further excavation or new construction.

1. Where new construction is not indicated, completely fill below-grade areas and voids resulting from building demolition operations with satisfactory soil materials according to backfill requirements in Division 2 Section "Earthwork."

B. Site Grading:  Uniformly rough grade area of demolished construction to a smooth surface, free from irregular surface changes.  Provide a smooth transition between adjacent existing grades and new grades.

3.7 REPAIRS

A. Promptly repair damage to adjacent buildings caused by demolition operations.

3.8 DISPOSAL OF DEMOLISHED MATERIALS

Retain one of first two paragraphs below.  Add other specific disposal, cleanup, or removal requirements to suit Project.

A. Remove demolition waste materials from Project site.  See Division 01 Section "Construction and Demolition Waste Management" for recycling and disposal of demolition waste.

Retain two subparagraphs below with either paragraph above.

1. Do not allow demolished materials to accumulate on-site.

2. Remove and transport debris in a manner that will prevent spillage on adjacent surfaces and areas.

B. Do not burn demolished materials.

3.9 CLEANING

A. Clean adjacent structures and improvements of dust, dirt, and debris caused by building demolition operations.  Return adjacent areas to condition existing before building demolition operations began.

END OF SECTION 02221

BUILDING DEMOLITION

02221 - 6

