Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications

SECTION 07811 – SPRAYED FIRE-RESISTIVE MATERIALS 
PART 1 -  GENERAL

1.1 SUMMARY
A. This Section includes SFRMs applied to surfaces that are concealed from view behind other construction when the Work is completed.

1.2 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Show extent of sprayed fire-resistive material for each construction and fire-resistance rating, applicable fire-resistive design designations of a qualified testing and inspecting agency acceptable to authorities having jurisdiction, and minimum thicknesses.

C. Product certificates.

D. Compatibility and adhesion test reports.

E. Research/evaluation reports.

F. Field quality-control test reports.

1.3 QUALITY ASSURANCE

A. Installer Qualifications:  A qualified installer approved by SFRM manufacturer to install manufacturer's products.  A manufacturer's willingness to sell its SFRM to Contractor or to an installer engaged by Contractor does not in itself confer qualification on the buyer.

B. SFRM Testing:  By a qualified testing and inspecting agency engaged by Contractor or manufacturer to test for compliance with specified requirements for performance and test methods.

1. SFRMs are randomly selected for testing from bags bearing the applicable classification marking of UL or another testing and inspecting agency acceptable to authorities having jurisdiction.

2. Testing is performed on specimens of SFRMs that comply with laboratory testing requirements specified in Part 2 and are otherwise identical to installed fire-resistive materials, including application of accelerant, sealers, topcoats, tamping, troweling, rolling, and water overspray, if any of these are used in final application.

3. Testing is performed on specimens whose application the independent testing and inspecting agency witnessed during preparation and conditioning.  Include in test reports a full description of preparation and conditioning of laboratory test specimens.

C. Compatibility and Adhesion Testing:  Engage a qualified testing and inspecting agency to test for compliance with requirements for specified performance and test methods.

1. Test for bond per ASTM E 736 and requirements in UL's "Fire Resistance Directory" for coating materials.  Provide bond strength indicated in referenced fire-resistance design, but not less than minimum specified in Part 2.

2. Verify that manufacturer, through its own laboratory testing or field experience, has not found primers or coatings to be incompatible with SFRM.

D. Fire-Test-Response Characteristics:  Where indicated, provide products identical to those tested for fire resistance per ASTM E 119 by a testing agency acceptable to authorities having jurisdiction.

Indicate rating, testing agency, and testing agency's design designation here or on Drawings.

1. Fire-Resistance Ratings:  Indicated by design designations from UL's "Fire Resistance Directory" or from the listings of another testing and inspecting agency.

2. Identify products with appropriate markings of applicable testing and inspecting agency.

E. Provide products containing no detectable asbestos as determined according to the method specified in 40 CFR 763, Subpart E, Appendix E, Section 1, "Polarized Light Microscopy."

Delete first paragraph and subparagraphs below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.

F. Preinstallation Conference:  Conduct conference at Project site.

1.4 PROJECT CONDITIONS

Revise first paragraph below if different temperature limits apply to products selected.

A. Environmental Limitations:  Do not apply SFRM when ambient or substrate temperature is 40 deg F (4 deg C) or lower unless temporary protection and heat are provided to maintain temperature at or above this level for 24 hours before, during, and for 24 hours after product application.

B. Ventilation:  Ventilate building spaces during and after application of SFRM.  Use natural means or, if they are inadequate, forced-air circulation until fire-resistive material dries thoroughly.

C. Sequence and coordinate application of SFRM with other related work specified in other Sections to comply with the following requirements:

1. Provide temporary enclosure as required to confine spraying operations and protect the environment.

2. Provide temporary enclosures for applications to prevent deterioration of fire-resistive material due to exposure to weather and to unfavorable ambient conditions for humidity, temperature, and ventilation.

3. Avoid unnecessary exposure of fire-resistive material to abrasion and other damage likely to occur during construction operations subsequent to its application.

4. Do not apply fire-resistive material to metal roof deck substrates until concrete topping, if any, has been completed.  For metal roof decks without concrete topping, do not apply fire-resistive material to metal roof deck substrates until roofing has been completed; prohibit roof traffic during application and drying of fire-resistive material.

5. Do not apply fire-resistive material to metal floor deck substrates until concrete topping has been completed.

6. Do not begin applying fire-resistive material until clips, hangers, supports, sleeves, and other items penetrating fire protection are in place.

7. Defer installing ducts, piping, and other items that would interfere with applying fire-resistive material until application of fire protection is completed.

8. Do not install enclosing or concealing construction until after fire-resistive material has been applied, inspected, and tested and corrections have been made to defective applications.

1.5 WARRANTY
A. Special Warranty:  Manufacturer's standard form, signed by Contractor and by Installer, in which manufacturer agrees to repair or replace SFRMs that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Cracking, flaking, spalling, or eroding in excess of specified requirements; peeling; or delaminating of SFRM from substrates.

b. Not covered under the warranty are failures due to damage by occupants and Owner's maintenance personnel, exposure to environmental conditions other than those investigated and approved during fire-response testing, and other causes not reasonably foreseeable under conditions of normal use.

Verify available warranties for units and components and insert number in subparagraph below.

2. Warranty Period:  Two years from date of Substantial Completion.

PART 2 -  PRODUCTS
2.1 CONCEALED SFRM

Revise title of this Article if desired.  Insert appropriate exposed fire-resistive products here if potential exists for exposure to abrasion, impact, high humidity, air erosion, corrosive atmosphere, etc., that products below cannot withstand.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs below.  Retain list of manufacturers and products with either of first two paragraphs; insert list of manufacturers if retaining third paragraph.  See Division 01 Section "Product Requirements."

A. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

1. Concealed Cementitious SFRM:

a. Carboline Co., Fireproofing Products Div.; Pyrolite 15 High Yield.

b. Grace, W. R. & Co. - Conn., Construction Products Div.; Monokote Type MK-6  .

c. Isolatek International Corp.; Cafco 300.

Retain second option in first paragraph below for selecting material by Contractor's option.

B. Material Composition:  Manufacturer's standard product:

1. Concealed Cementitious SFRM:  Factory-mixed, dry formulation of gypsum or portland cement binders, additives, and lightweight mineral or synthetic aggregates mixed with water at Project site to form a slurry or mortar for conveyance and application.

Retain subparagraph above for cementitious type.  Retain subparagraph below for sprayed-fiber type.  Coordinate with fire-resistance design designated for Project.

C. Physical Properties:  Minimum values, unless otherwise indicated, or higher values required to attain designated fire-resistance ratings, measured per standard test methods referenced with each property as follows:

1. Dry Density:  15 lb/cu. ft. (240 kg/cu. m) for average and individual densities, or greater if required to attain fire-resistance ratings indicated, per ASTM E 605 or AWCI Technical Manual 12-A, Section 5.4.5, "Displacement Method."

2. Thickness:  Minimum average thickness required for fire-resistance design indicated according to the following criteria, but not less than 0.375 inch (9 mm), per ASTM E 605:

a. Where the referenced fire-resistance design lists a thickness of 1 inch (25 mm) or more, the minimum allowable individual thickness of SFRM is the design thickness minus 0.25 inch (6 mm).

b. Where the referenced fire-resistance design lists a thickness of less than 1 inch (25 mm) but more than 0.375 inch (9 mm), the minimum allowable individual thickness of SFRM is the greater of 0.375 inch (9 mm) or 75 percent of the design thickness.

c. No reduction in average thickness is permitted for those fire-resistance designs whose fire-resistance ratings were established at densities of less than 15 lb/cu. ft. (240 kg/cu. m).

Value in first subparagraph below is minimum bond strength permitted by IBC and NFPA 5000.  Codes require bond strength value per designated fire-resistance design, but not less than 150 lbf/sq. ft. (7.2 kPa).

3. Bond Strength:  150 lbf/sq. ft. (7.2 kPa) minimum per ASTM E 736 based on laboratory testing of 0.75-inch (19-mm) minimum thickness of SFRM.

4. Compressive Strength:  5.21 lbf/sq. in. (35.9 kPa) minimum per ASTM E 761.  Minimum thickness of SFRM tested shall be 0.75 inch (19 mm) and minimum dry density shall be as specified but not less than 15 lb/cu. ft. (240 kg/cu. m).

5. Corrosion Resistance:  No evidence of corrosion per ASTM E 937.

6. Deflection:  No cracking, spalling, or delamination per ASTM E 759.

7. Effect of Impact on Bonding:  No cracking, spalling, or delamination per ASTM E 760.

8. Air Erosion:  Maximum weight loss of 0.025 g/sq. ft. (0.270 g/sq. m) in 24 hours per ASTM E 859.  For laboratory tests, minimum thickness of SFRM is 0.75 inch (19 mm), maximum dry density is 15 lb/cu. ft. (240 kg/cu. m), test specimens are not prepurged by mechanically induced air velocities, and tests are terminated after 24 hours.

9. Fire-Test-Response Characteristics:  Provide SFRM with the following surface-burning characteristics as determined by testing identical products per ASTM E 84 by UL or another testing and inspecting agency acceptable to authorities having jurisdiction:

a. Flame-Spread Index:  10 or less.

b. Smoke-Developed Index:  0.

Test method in subparagraph below is an example for special environments such as hospitals or where indoor air quality is an issue.  Verify, with manufacturer, test method and availability of microbial inhibitors for selected products.

2.2 AUXILIARY FIRE-RESISTIVE MATERIALS

A. General:  Provide auxiliary fire-resistive materials that are compatible with SFRM and substrates and are approved by UL or another testing and inspecting agency acceptable to authorities having jurisdiction for use in fire-resistance designs indicated.

B. Substrate Primers:  For use on each substrate and with each sprayed fire-resistive product, provide primer that complies with one or more of the following requirements:

1. Primer's bond strength complies with requirements specified in UL's "Fire Resistance Directory" for coating materials based on a series of bond tests per ASTM E 736.

2. Primer is identical to those used in assemblies tested for fire-test-response characteristics of SFRM per ASTM E 119 by UL or another testing and inspecting agency acceptable to authorities having jurisdiction.

C. Adhesive for Bonding Fire-Resistive Material:  Product approved by manufacturer of SFRM.

D. Metal Lath:  Expanded metal lath fabricated from material of weight, configuration, and finish required to comply with fire-resistance designs indicated and fire-resistive material manufacturer's written recommendations.  Include clips, lathing accessories, corner beads, and other anchorage devices required to attach lath to substrates and to receive SFRM.

E. Reinforcing Fabric:  Glass- or carbon-fiber fabric of type, weight, and form required to comply with fire-resistance designs indicated; approved and provided by manufacturer of SFRM.

F. Sealer for Sprayed-Fiber Fire-Resistive Material:  Transparent-drying, water-dispersible, tinted protective coating recommended in writing by manufacturer of sprayed-fiber fire-resistive material.

Subparagraph below is one example of an Isolatek product whose use for application over specific Isolatek products must be verified with manufacturer.  Coordinate subparagraph with manufacturers named in other Part 2 articles for single-source responsibility for tested systems.

G. Topcoat:  Type recommended in writing by manufacturer of each SFRM.

PART 3 -  EXECUTION
3.1 INSTALLATION
A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for substrates and other conditions affecting performance of work.  A substrate is in satisfactory condition if it complies with the following:

1. Substrates comply with requirements in the Section where the substrate and related materials and construction are specified.

2. Substrates are free of dirt, oil, grease, release agents, rolling compounds, mill scale, loose scale, incompatible primers, incompatible paints, incompatible encapsulants, or other foreign substances capable of impairing bond of fire-resistive materials with substrates under conditions of normal use or fire exposure.

3. Objects penetrating fire-resistive material, including clips, hangers, support sleeves, and similar items, are securely attached to substrates.

4. Substrates are not obstructed by ducts, piping, equipment, and other suspended construction that will interfere with applying fire-resistive material.

5. Proceed with installation only after unsatisfactory conditions have been corrected.

First two paragraphs below contain recommendations from ASTM E 1513 "Practice for Application of Sprayed Fire-Resistive Materials (SFRMs)." Delete first paragraph if not applicable.

B. Conduct tests according to fire-resistive material manufacturer's written recommendations to verify that substrates are free of substances capable of interfering with bond.

C. Cover other work subject to damage from fallout or overspray of fire-resistive materials during application.

D. Clean substrates of substances that could impair bond of fire-resistive material, including dirt, oil, grease, release agents, rolling compounds, mill scale, loose scale, and incompatible primers, paints, and encapsulants.

Delete first paragraph below if fire-resistive products selected are fire tested over unprimed steel and other substrates, which is generally true for interior concealed fire-resistive products.

E. Prime substrates where recommended in writing by SFRM manufacturer unless compatible shop primer has been applied and is in satisfactory condition to receive SFRM.

F. Install metal lath and reinforcing fabric, as required, to comply with fire-resistance ratings and fire-resistive material manufacturer's written recommendations for conditions of exposure and intended use.  Securely attach lath and fabric to substrate in position required for support and reinforcement of fire-resistive material.  Use anchorage devices of type recommended in writing by SFRM manufacturer.  Attach accessories where indicated or required for secure attachment of lath and fabric to substrate.

First paragraph below generally applies to metal-deck applications for certain fire-resistive products; delete if not applicable.

G. Coat substrates with bonding adhesive before applying fire-resistive material where required to achieve fire-resistance rating or as recommended in writing by SFRM manufacturer for material and application indicated.

H. Extend fire-resistive material in full thickness over entire area of each substrate to be protected.  Unless otherwise recommended in writing by SFRM manufacturer, install body of fire-resistive covering in a single course.

I. Spray apply fire-resistive materials to maximum extent possible.  Following the spraying operation in each area, complete the coverage by trowel application or other placement method recommended in writing by SFRM manufacturer.

J. Where sealers are used, apply products that are tinted to differentiate them from SFRM over which they are applied.

K. Apply concealed SFRM in thicknesses and densities not less than those required to achieve fire-resistance ratings designated for each condition, but apply in greater thicknesses and densities if specified in Part 2 "Concealed SFRM" Article.

In first four paragraphs below, delete provisions for water overspray, sealers, and topcoats if not required for concealed applications for types of fire-resistive products specified.  Retain option in any retained paragraph if some products require provision and some do not.  Insert additional requirements if other procedures are applicable to concealed applications.

L. Apply water overspray to concealed sprayed-fiber fire-resistive material as required to obtain designated fire-resistance rating.

M. Cure concealed SFRM according to product manufacturer's written recommendations.

N. Apply sealer to concealed SFRM.

O. Apply topcoat to concealed SFRM.

P. Immediately after completing spraying operations in each containable area of Project, remove material overspray and fallout from surfaces of other construction and clean exposed surfaces to remove evidence of soiling.

Q. Repair or replace work that has not successfully protected steel.

3.2 FIELD QUALITY CONTROL

Retain first option in paragraph below if Owner engages special inspector.  If authorities having jurisdiction permit Contractor to engage special inspector, retain second option and retain option for submitting special inspection reports in "Submittals" Article.

A. Special Inspections:  Owner will engage  a qualified special inspector to perform the following special inspections and prepare reports:

1. SFRM.

Retain first option in first paragraph below if Owner engages testing agency.  If authorities having jurisdiction permit Contractor to engage testing agency, retain second option and retain option for submitting field quality-control reports in "Submittals" Article.

B. Testing Agency:  Owner will engage  a qualified testing agency to perform tests and inspections and prepare test reports.

1. Testing and inspecting agency will interpret tests and state in each report whether tested work complies with or deviates from requirements.

C. Tests and Inspections:  Testing and inspecting of completed applications of SFRM shall take place in successive stages, in areas of extent and using methods as follows.  Do not proceed with application of SFRM for the next area until test results for previously completed applications of SFRM show compliance with requirements.  Tested values must equal or exceed values indicated and required for approved fire-resistance design.

Retain tests and inspections in subparagraphs and associated subparagraphs below, which are examples, per IBC, for cementitious sprayed and sprayed-fiber fire-resistive materials only.  Revise to suit products selected and requirements of Project and of authorities having jurisdiction.  See Evaluations.  Add testing and inspection requirements, if any, for intumescent mastics.

1. Thickness for Structural Frame Members:  From a sample of 25 percent of structural members per floor, taking 9 measurements at a single cross section for structural frame beams or girders, 7 measurements of a single cross section for joists and trusses, and 12 measurements of a single cross section for columns per ASTM E 605.

2. Bond Strength for Structural Framing Members:  For each 10,000-sq. ft. (929 sq. m) area, or partial area, on each floor, cohesion and adhesion from one sample of size indicated for determining thickness of each type of construction and structural framing member, per ASTM E 736.

a. Field test SFRM that is applied to flanges of wide-flange, structural-steel members on surfaces matching those that will exist for remainder of steel receiving fire-resistive material.

b. If surfaces of structural steel receiving SFRM are primed or otherwise painted for coating materials, perform series of bond tests specified in UL's "Fire Resistance Directory." Provide bond strength indicated in referenced UL fire-resistance criteria, but not less than 150 lbf/sq. ft. (7.2 kPa) minimum per ASTM E 736.

3. If testing finds applications of SFRM are not in compliance with requirements, testing and inspecting agency will perform additional random testing to determine extent of noncompliance.

D. Remove and replace applications of SFRM that do not pass tests and inspections for cohesion and adhesion, for density, or for both and retest as specified above.

E. Apply additional SFRM, per manufacturer's written instructions, where test results indicate that thickness does not comply with specified requirements, and retest as specified above.

END OF SECTION 07811

SPRAYED FIRE-RESISTIVE MATERIALS

07811 - 7

