Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications

SECTION 07841 – THROUGH-PENETRATION FIRESTOP SYSTEM
PART 1 -  GENERAL

1.1 SUMMARY
A. Extent firestopping work for fireproofing to include:  penetrations where mechanical,              electrical piping, conduit, cabletrays, ducts, other trade items pierce fire rated walls, and           smoke barriers, and construction gaps. 

B. Related Items:  Expansion joint covers, mechanical and electrical devices requiring          firestopping through fire rated walls, partitions such as fire dampers, electrical cabletrays, etc.

C. References:  U.L. Fire Resistance Directory:  Through-penetration firestop devices (XHCR);        Fire resistance ratings (BXUV); Through-penetration firestop systems (XHEZ); Fill, void or      cavity material (XHHW). Warnock Hersey. American Society For Testing and Materials Standards:  ASTM E814-88:  Standard Test Method For Fire Tests of Through-Penetration Firestops.

1.2 DEFINITIONS
A. Assembly:  Particular arrangement of materials specific to given type of construction described      or detailed in referenced documents.

B. Barriers:  Time rated firewalls, partitions, smoke barrier walls, partitions.  

C. Firestopping:  Methods, materials applied in penetrations, unprotected openings to limit spread of heat, fire, gasses, smoke.

D. Penetration:  Opening or foreign material passing through or into barrier or structural floor such that full thickness of rated materials not obtained.

E. System: Specific products, applications, classified, numbered by Underwriters Laboratories, Inc.    to close specific barrier penetrations.

F. Sleeve:  Metal fabrication or pipe section extending through thickness of barrier, used to permanently guard penetration. Sleeves described as part of penetrating system in other        sections and may or may not be required.

1.3 SYSTEM DESCRIPTION
A. Design Requirements:  Smoke barrier and Fire-rated construction: Maintain barrier,                 structural floor fire resistance ratings including resistance to cold smoke at all penetrations, connections with other surfaces, types of construction, at all separations required to permit       building movement, sound or vibration absorption, and at other construction gaps.

1.4 QUALITY ASSURANCE
A. Firm experienced in installation, application of systems similar in complexity to those required        for this project. Acceptable to or licensed by manufacturer, state or local authority where applicable. At least two (2) years experience with systems. Successfully completed at least          five (5) comparable scale projects using this system.

B. Local and state regulatory requirements:  Submit forms or acceptance for proposed         assemblies not conforming to specific UL Firestop System numbers, or UL classified devices.

C. Materials tested to provide fire rating at least equal to that of construction.

1.5 DELIVERY AND STORAGE

A. Deliver products in original unopened packaging with legible manufacturer’s identification. Coordinate delivery with scheduled installation date, allow minimum storage at site. Store materials in clean, dry, ventilated location. Protect from soiling, abuse, moisture, freezing when required. Follow manufacturer's instructions.

1.6 SUBMITTALS
A. Product data:    Manufacturer's specifications, technical data including detailed specification of construction, fabrication and instructions.

1.7 SHOP DRAWINGS
A. Indicate dimensions, descriptions of materials, finishes, general construction, specific modifications, component connections, anchorage methods, hardware, installation    procedures,  plus  following  specific  requirements:
1. Details of each proposed assembly identifying intended products, applicable UL System number, or UL classified devices.

2. Manufacturer or Manufacturer's Representative provide qualified engineering judgements, drawings related to non-standard applications as needed.

3. Upon request, provide samples of material and products to be used.

PART 2 -  PRODUCTS
2.1 THROUGH-PENETRATION FIRESTOPPING OF FIRE-RATED CONSTRUCTION

A. Systems or devices as specified and manufactured. By unique Fire Stop products, Inc. other manufacturers are acceptable, subject to prior approval, and that their system(s) conforms to construction type, penetrant type, annular space requirements, fire rating involved in each separate instance, and that system be symmetrical for wall applications. Systems or devices       must be asbestos-free. Mortar systems must be Warnock Hersey approved.

2.2 ADDITIONAL REQUIREMENTS

A. Withstand passage of cold smoke either as inherent property of system, or by use of separate product included as part of U.L. system or device, designed to perform this function.

B. Acceptable manufacturers and products are those listed in U.L. Fire Resistance directory for         U.L. System involved or Mortar systems approved by Warnock Hersey.  All firestopping products from single manufacturer.

2.3 CONSTRUCTION-GAP FIRESTOPPING OF FIRE-RATED CONSTRUCTION

A. Firestopping at construction gaps between tops of partitions, underside of structural systems.  Firestopping at construction gaps between partitions, adjacent partitions.

B. Penetrator Devices and Cable Tray Penetrations:
1. Basic – Penetrator System #W-L-3137 as manufactured by Unique Fire Stop                     Products, Inc. – Robertsdale, AL 36567.

2. U.L. Fire Rated for penetrating fire partitions shall be same rating(s) as partition. Refer to drawing for partition ratings.

3. Four-inch (4”) diameter assembly where two (2) sleeves will be provided in line of the      cable tray. The cable tray shall be cut off short of the sleeves on both sides of the wall.  The gap between the sleeves and the wall penetration shall be fire caulked by the Contractor and he will install the collars around the sleeves at the walls. He will also     provide a plastic bushing around the edges on both ends of the sleeve. Owner will do          the cabling in the cable trays and through the sleeves and be responsible for caulking around the cables and sealing the sleeves completely to meet code requirements.         Should a sleeve not be used, then the Owner shall fire caulk the open sleeve. This method shall be used for all open cable penetrations through fire rated walls. Smoke Barrier Walls are considered to be 1-hour fire rated walls.
4. A similar, Contractor-fabricated, sleeve that resembles the system described above            will be used for all non-fire rated walls are expected to be penetrated. The caulking materials used do not have to be fire rated.
C. Cable Tray Wall Penetrators:

1. Substitute – Should the Owner request this type penetration, Contractor shall submit a     cost per each unit (including taxes, overhead, etc.) in the space provided in the form           of proposal.

2. System W-L-4029 F for fire rated walls and System W-L-4029 T for non-fire rated walls.

3. Product of Unique Fire Stop Products, Inc. – Robertsdale, AL 36567. Materials and methods described in U300 and U400 Series wall or partition designs in U.L. Fire   Resistive Directory.  Refer to drawings for partitions ratings.

2.4 ACCESSORIES
A. Fill, void or cavity materials:    As classified under category XHHW in U.L. Fire Resistance Director or Mortars as approved by Warnock Hersey.  Forming materials:   As classified  under  category  XHKU  in U.L.  Fire Resistance Directory.
PART 3 -  EXECUTION
3.1 VERIFICATION OF CONDITIONS

A. Examine areas, conditions under which work performed, identify conditions detrimental to      proper or timely completion. Verify barrier penetrations properly sized, in suitable condition for application of materials. Do not proceed until unsatisfactory conditions corrected. Proceed          with installation only after penetrations of substrate, supporting brackets installed.

3.2 ENVIRONMENTAL REQUIREMENTS

A. Provide adequate ventilation if using solvent. Provide forced air ventilation during installation if required by manufacturer. Keep flammable materials away from sparks or flame. Provide masking, drop cloths to prevent contamination of adjacent surfaces by firestopping materials. Comply with manufacturer’s recommendations for temperature, humidity conditions before,        during and after installation of firestopping.

3.3 PREPARATION
A. Clean surfaces in contact with penetration seal materials, of dirt, grease, oil, loose materials,        rust, other substances that may affect proper fitting, adhesion, or required fire resistance.

3.4 INSTALLATION
A. Firestopping:  Install penetration seal materials in accord printed instructions U.L. Fire        Resistance Directory of Mortars per Warnock Hersey approval and in accord with manufacturer’s instruction.  Seal holes or voids made by penetrations to ensure an effective smoke barrier.  Protect materials from damage on surfaces subject to traffic. Where large openings created in walls, floors to permit installation of pipes, ducts or other items, close unused portions of opening with firestopping material tested for application. See U.L. Fire Resistance Directory, Warnock Hersey approvals.  Install smoke stopping specified for firestopping.

3.5 FIELD QUALITY CONTROL

A. Examine penetration sealed areas to ensure proper installation before concealing or                enclosing areas. Keep areas of work accessible until inspection by applicable code              authorities. Perform under this section patching, repairing of firestopping caused by cutting or penetration by other trades.

3.6 ADJUSTING AND CLEANING

A. Clean up spills of liquid components.  Neatly cut, trim materials as required. Remove equipment, materials, debris, leaving area in undamaged, clean condition.
END OF SECTION 07841

THROUGH-PENETRATION FIRESTOP SYSTEM

07841 - 4

