Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications

SECTION 08110 – STEEL DOORS AND FRAMES 
PART 1 -  GENERAL

1.1 SUMMARY
A. Section Includes:

1. Standard hollow metal doors and frames.

1.2 SUBMITTALS
A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Include elevations, door edge details, frame profiles, metal thicknesses, preparations for hardware, and other details.

C. Schedule:  Prepared by or under the supervision of supplier.

1.3 QUALITY ASSURANCE

A. Fire-Rated Door Assemblies:  Assemblies complying with NFPA 80 that are listed and labeled by a qualified testing agency, for fire-protection ratings indicated. based on testing at positive pressure  according to NFPA 252 or UL 10C.

B. Smoke-Control Door Assemblies:  Comply with NFPA 105 or UL 1784.

PART 2 -  PRODUCTS
2.1 MATERIALS
A. Cold-Rolled Steel Sheet:  ASTM A 1008/A 1008M, CS, Type B; suitable for exposed applications.

B. Hot-Rolled Steel Sheet:  ASTM A 1011/A 1011M, CS, Type B.

C. Metallic-Coated Steel Sheet:  ASTM A 653/A 653M, Commercial Steel (CS), Type B; with minimum  G60 (Z180) or A60 (ZF180) metallic coating.

D. Frame Anchors:  ASTM A 591/A 591M, Commercial Steel (CS), 40Z (12G) coating designation; mill phosphatized.

1. For anchors built into exterior walls, steel sheet complying with ASTM A 1008/A 1008M or ASTM A 1011/A 1011M, hot-dip galvanized according to ASTM A 153/A 153M, Class B.

E. Inserts, Bolts, and Fasteners:  Hot-dip galvanized according to ASTM A 153/A 153M.

F. Mineral-Fiber Insulation:  ASTM C 665, Type I.

2.2 STANDARD HOLLOW METAL DOORS

A. General:  Comply with ANSI/SDI A250.8.

1. Design:  Embossed panel unless otherwise indicated.

2. Core Construction:  Manufacturer's standard kraft-paper honeycomb, polystyrene, polyurethane, polyisocyanurate, mineral-board, or vertical steel-stiffener core.

a. Fire Door Core:  As required to provide fire-protection and temperature-rise ratings indicated.

b. Thermal-Rated (Insulated) Doors:  R-value of not less than 6.0 deg F x h x sq. ft./Btu (1.057 K x sq. m/W) when tested according to ASTM C 1363.

3. Vertical Edges for Single-Acting Doors:  Manufacturer's standard.

4. Top and Bottom Edges:  Closed with flush or inverted 0.042-inch- (1.0-mm-) thick, end closures or channels of same material as face sheets.

5. Tolerances:  SDI 117, "Manufacturing Tolerances for Standard Steel Doors and Frames."

B. Exterior Doors and Interior Doors at First Floor:  Face sheets fabricated from metallic-coated steel sheet.  Comply with ANSI/SDI A250.8 for level and model and ANSI/SDI A250.4 for physical performance level:

1. Exterior Doors:  Level 3 and Physical Performance Level A (Extra Heavy Duty), Model 1 (Full Flush).

2. Interior Doors at First Floor:  Level 2 and Physical Performance Level B (Heavy Duty), Model 1 (Full Flush).

C. Interior Doors above First Floor:  Face sheets fabricated from cold-rolled steel sheet.  Provide doors complying with requirements indicated below by referencing ANSI/SDI A250.8 for level and model and ANSI/SDI A250.4 for physical performance level:

1. All interior locations above first floor other than stairwells:  Level 2 and Physical Performance Level B (Heavy Duty), Model 1 (Full Flush).

2. All interior entrances to stairwells above the first floor:  Level 3 and Physical Performance Level A (Extra Heavy Duty), Model 1 (Full Flush) .

D. Hardware Reinforcement:  ANSI/SDI A250.6.

2.3 STANDARD HOLLOW METAL FRAMES

A. General:  Comply with ANSI/SDI A250.8.

B. Exterior Frames:  Fabricated from metallic-coated steel sheet.

1. Fabricate frames with mitered or coped corners.

2. Fabricate frames as full profile welded unless otherwise indicated.

3. Frames for Level 3 Steel Doors:  0.053-inch- (1.3-mm-) thick steel sheet.

C. Interior Frames:  Fabricated from cold-rolled steel sheet.

1. Fabricate frames with mitered or coped corners.

2. Frames for Level 2 Steel Doors:  0.053-inch- (1.3-mm-) thick steel sheet.

3. Frames for Level 3 Steel Doors:  0.053-inch- (1.3-mm-) thick steel sheet.

4. Frames for Wood Doors:  0.053-inch- (1.3-mm-)  thick steel sheet.

D. Hardware Reinforcement:  ANSI/SDI A250.6.

2.4 FRAME ANCHORS
A. Jamb Anchors:

Retain types in four subparagraphs below to suit Project.

Wire anchors in first subparagraph below are often used to permit unobstructed grouting of frames.

1. Masonry Type:  Adjustable strap-and-stirrup or T-shaped anchors to suit frame size, not less than 0.042 inch (1.0 mm) thick, with corrugated or perforated straps not less than 2 inches (50 mm) wide by 10 inches (250 mm) long; or wire anchors not less than 0.177 inch (4.5 mm) thick.

2. Stud-Wall Type:  Designed to engage stud, welded to back of frames; not less than 0.042 inch (1.0 mm) thick.

3. Compression Type for Drywall Slip-on Frames:  Adjustable compression anchors.

4. Postinstalled Expansion Type for In-Place Concrete or Masonry:  Minimum 3/8-inch- (9.5-mm-) diameter bolts with expansion shields or inserts.  Provide pipe spacer from frame to wall, with throat reinforcement plate, welded to frame at each anchor location.

B. Floor Anchors:  Formed from same material as frames, not less than 0.042 inch (1.0 mm) thick, and as follows:

1. Monolithic Concrete Slabs:  Clip-type anchors, with two holes to receive fasteners.

2.5 STOPS AND MOLDINGS

A. Moldings for Glazed Lites in Doors:  Minimum 0.032 inch (0.8 mm) thick, same material as door face sheet.

B. Fixed Frame Moldings:  Formed integral with hollow metal frames, a minimum of 5/8 inch (16 mm) high unless otherwise indicated.

C. Loose Stops for Glazed Lites in Frames:  Minimum 0.032 inch (0.8 mm) thick, same material as frames.

Retain paragraph below if applicable.  Do not use for labeled or other restricted openings.  Terminated stops are also called "hospital stops."

D. Terminated Stops:  Where indicated, terminate stops 6 inches (152 mm) above finish floor with a 45-degree angle cut, and close open end of stop with steel sheet closure.  Cover opening in extension of frame with welded-steel filler plate, with welds ground smooth and flush with frame.

2.6 LOUVERS

A. Provide sightproof louvers for interior doors, where indicated, that comply with SDI 111C, with blades or baffles formed of 0.020-inch- (0.5-mm-) thick, cold-rolled steel sheet set into 0.032-inch- (0.8-mm-) thick steel frame.  Provide galvanized louvers where frames/doors required to be galvanized.
See Evaluations for discussion of fire-rated louvers.

1. Fire-Rated Automatic Louvers:  Movable blades closed by actuating fusible link, and listed and labeled for use in fire-rated door assemblies of type and fire-resistance rating indicated.

2.7 ACCESSORIES

Retain paragraphs in this article to suit Project; revise if necessary.

A. Mullions and Transom Bars:  Join to adjacent members by welding or rigid mechanical anchors.

B. Ceiling Struts:  Minimum 1/4-inch-thick by 1-inch- (6.4-mm-thick by 25.4-mm-) wide steel.

C. Grout Guards:  Formed from same material as frames, not less than 0.016 inch (0.4 mm) thick.

2.8 FABRICATION
A. Tolerances:  Fabricate hollow metal work to tolerances indicated in SDI 117.

B. Hollow Metal Doors:

1. Exterior Doors:  Provide weep-hole openings in bottom of exterior doors.  Seal joints in top edges of doors against water penetration.

2. Glazed Lites:  Factory cut openings in doors.

Retain subparagraph below if astragals are required for fire-protection rating.

3. Astragals:  Provide overlapping astragal on one leaf of pairs of doors where required by NFPA 80 for fire-performance rating or where indicated.

C. Hollow Metal Frames:  Where frames are fabricated in sections, provide alignment plates or angles at each joint, fabricated of same thickness metal as frames.

1. Welded Frames:  Weld flush face joints continuously; grind, fill, dress, and make smooth, flush, and invisible.

2. Provide countersunk, flat- or oval-head exposed screws and bolts for exposed fasteners unless otherwise indicated.

3. Grout Guards:  Weld guards to frame at back of hardware mortises in frames to be grouted.

4. Floor Anchors:  Weld anchors to bottom of jambs and mullions with at least four spot welds per anchor.

5. Jamb Anchors:  Provide number and spacing of anchors as follows:

Fire ratings may require additional anchors.

a. Masonry Type:  Locate anchors not more than 18 inches (457 mm) from top and bottom of frame.  Space anchors not more than 32 inches (813 mm) o.c. and as follows:

1) Three anchors per jamb from 60 to 90 inches (1524 to 2286 mm) high.

2) Four anchors per jamb from 90 to 120 inches (2286 to 3048 mm) high.

3) Four anchors per jamb plus 1 additional anchor per jamb for each 24 inches (610 mm) or fraction thereof above 120 inches (3048 mm) high.

b. Stud-Wall Type:  Locate anchors not more than 18 inches (457 mm) from top and bottom of frame.  Space anchors not more than 32 inches (813 mm) o.c. and as follows:

1) Four anchors per jamb from 60 to 90 inches (1524 to 2286 mm) high.

2) Two anchors per head for frames more than 42 inches (1066 mm) wide and mounted in metal-stud partitions.

c. Compression Type:  Not less than two anchors in each jamb.

6. Door Silencers:  Except on weather-stripped doors, drill stops to receive door silencers.

a. Single-Door Frames:  Three door silencers.

b. Double-Door Frames:  Two door silencers.

D. Hardware Preparation:  Factory prepare hollow metal work to receive templated mortised hardware according to the Door Hardware Schedule and templates furnished as specified in Division 08 Section "Door Hardware."

1. Locate hardware as indicated, or if not indicated, according to ANSI/SDI A250.8.

2. Reinforce doors and frames to receive nontemplated, mortised and surface-mounted door hardware.

3. Comply with applicable requirements in ANSI/SDI A250.6 and ANSI/DHI A115 Series specifications for preparation of hollow metal work for hardware.

4. Coordinate locations of conduit and wiring boxes for electrical connections with Division 26 electrical Sections.

E. Stops and Moldings:  Provide stops and moldings around glazed lites where required.  Form corners of stops and moldings with butted or mitered hairline joints.

1. Single Glazed Lites:  Provide fixed stops and moldings welded on secure side of hollow metal work.

2. Multiple Glazed Lites:  Provide fixed and removable stops and moldings so that each glazed lite is capable of being removed independently.

3. Provide fixed frame moldings on outside of exterior and on secure side of interior doors and frames.

4. Provide loose stops and moldings on inside of hollow metal work.

5. Coordinate rabbet width between fixed and removable stops with type of glazing and type of installation required.

2.9 STEEL FINISHES
A. Prime Finish:  Apply manufacturer's standard primer immediately after cleaning and pretreating.

1. Shop Primer:  ANSI/SDI A250.10.

PART 3 -  EXECUTION
3.1 INSTALLATION
A. Hollow Metal Frames:  Comply with ANSI/SDI A250.11.

1. Set frames accurately in position, plumbed, aligned, and braced securely until permanent anchors are set.  After wall construction is complete, remove temporary braces, leaving surfaces smooth and undamaged.

a. At fire-protection-rated openings, install frames according to NFPA 80.

b. Where frames are fabricated in sections because of shipping or handling limitations, field splice at approved locations by welding face joint continuously; grind, fill, dress, and make splice smooth, flush, and invisible on exposed faces.

c. Install frames with removable glazing stops located on secure side of opening.

d. Install door silencers in frames before grouting.

e. Remove temporary braces necessary for installation only after frames have been properly set and secured.

f. Check plumbness, squareness, and twist of frames as walls are constructed.  Shim as necessary to comply with installation tolerances.

g. Field apply bituminous coating to backs of frames that are filled with grout containing antifreezing agents.

2. Floor Anchors:  Provide floor anchors for each jamb and mullion that extends to floor, and secure with postinstalled expansion anchors.

a. Floor anchors may be set with powder-actuated fasteners instead of postinstalled expansion anchors if so indicated and approved on Shop Drawings.

3. Metal-Stud Partitions:  Solidly pack mineral-fiber insulation behind frames.

Retain one or both of first two subparagraphs below if grouted frames are required.  See Evaluations for discussion.

4. Masonry Walls:  Coordinate installation of frames to allow for solidly filling space between frames and masonry with grout.

5. In-Place Masonry Construction:  Secure frames in place with postinstalled expansion anchors.  Countersink anchors, and fill and make smooth, flush, and invisible on exposed faces.

6. In-Place Gypsum Board Partitions:  Secure frames in place with postinstalled expansion anchors through floor anchors at each jamb.  Countersink anchors, and fill and make smooth, flush, and invisible on exposed faces.

7. Ceiling Struts:  Extend struts vertically from top of frame at each jamb to overhead structural supports or substrates above frame unless frame is anchored to masonry or to other structural support at each jamb.  Bend top of struts to provide flush contact for securing to supporting construction.  Provide adjustable wedged or bolted anchorage to frame jamb members.

8. Installation Tolerances:  Adjust hollow metal door frames for squareness, alignment, twist, and plumb to the following tolerances:

a. Squareness:  Plus or minus 1/16 inch (1.6 mm), measured at door rabbet on a line 90 degrees from jamb perpendicular to frame head.

b. Alignment:  Plus or minus 1/16 inch (1.6 mm), measured at jambs on a horizontal line parallel to plane of wall.

c. Twist:  Plus or minus 1/16 inch (1.6 mm), measured at opposite face corners of jambs on parallel lines, and perpendicular to plane of wall.

d. Plumbness:  Plus or minus 1/16 inch (1.6 mm), measured at jambs at floor.

B. Hollow Metal Doors:  Fit hollow metal doors accurately in frames, within clearances specified below.  Shim as necessary.

1. Non-Fire-Rated Standard Steel Doors:

a. Jambs and Head:  1/8 inch (3 mm) plus or minus 1/16 inch (1.6 mm).

b. Between Edges of Pairs of Doors:  1/8 inch (3 mm) plus or minus 1/16 inch (1.6 mm).

c. Between Bottom of Door and Top of Threshold:  Maximum 3/8 inch (9.5 mm).

d. Between Bottom of Door and Top of Finish Floor (No Threshold):  Maximum 3/4 inch (19 mm).

2. Fire-Rated Doors:  Install doors with clearances according to NFPA 80.

3. Smoke-Control Doors:  Install doors according to NFPA 105.

C. Glazing:  Comply with installation requirements in Division 08 Section "Glazing" and with hollow metal manufacturer's written instructions.

1. Secure stops with countersunk flat- or oval-head machine screws spaced uniformly not more than 9 inches (230 mm) o.c. and not more than 2 inches (50 mm) o.c. from each corner.

3.2 ADJUSTING AND CLEANING

A. Final Adjustments:  Check and readjust operating hardware items immediately before final inspection.  Leave work in complete and proper operating condition.  Remove and replace defective work, including hollow metal work that is warped, bowed, or otherwise unacceptable.

B. Prime-Coat Touchup:  Immediately after erection, sand smooth rusted or damaged areas of prime coat and apply touchup of compatible air-drying, rust-inhibitive primer.

C. Metallic-Coated Surfaces:  Clean abraded areas and repair with galvanizing repair paint according to manufacturer's written instructions.

END OF SECTION 08110

STEEL DOORS AND FRAMES

08110 - 6

