Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications


Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 14210 - ELECTRIC TRACTION ELEVATORS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes electric traction passenger elevators.

B. See Division 09 Section "Resilient Flooring" for finish flooring in elevator cars.

1.2 SUBMITTALS

A. Product Data:  Include capacities, sizes, performances, operations, safety features, finishes, and similar information.

B. Shop Drawings:  Show plans, elevations, sections, and large-scale details indicating service at each landing, machine room layout, coordination with building structure, relationships with other construction, and locations of equipment and signals.  Indicate loads imposed on building structure at points of support, and maximum and average power demands.

C. Samples:  For exposed finishes.

D. Manufacturer Certificates:  Signed by elevator manufacturer certifying that hoistway, pit, and machine room layout and dimensions, as shown on Drawings, and electrical service, as shown and specified, are adequate for elevator system being provided.

E. Operation and maintenance data.

F. Inspection and Acceptance Certificates and Operating Permits:  As required by authorities having jurisdiction for normal, unrestricted elevator use.

1.3 QUALITY ASSURANCE

Always retain code-compliance requirement in paragraph below.  The 2003 International Building Code (IBC) requires compliance with ASCE 7-02, and the 2000 IBC has similar requirements.

A. Regulatory Requirements:  Comply with ASME A17.1 and elevator design requirements for earthquake loads in ASCE 7.

Usually retain one of two standards in paragraph below.

B. Accessibility Requirements:  Comply with Section 4.10 in the U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG)." 

1.4 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Manufacturer's Warranty:  Manufacturer's standard form in which manufacturer agrees to repair, restore, or replace defective elevator work within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period:  One year from date of Substantial Completion.

1.5 MAINTENANCE SERVICE

To avoid problems, initial maintenance service and warranty should run concurrently.

A. Initial Maintenance Service:  Beginning at Substantial Completion, provide one year's full maintenance service by skilled employees of elevator Installer.  Include monthly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper elevator operation at rated speed and capacity.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Basis-of-Design Product:  Subject to compliance with requirements, provide Otis Elevator Co., Machnie Room-less Gen2™ traction passenger elevator or a comparable product.

2.2 SYSTEMS AND COMPONENTS

A. General:  Provide manufacturer's standard elevator systems, including standard components published by manufacturer as included in standard preengineered elevator systems and as required for complete system.

B. Machine:  AC gearless machine, with a synchronous permanent-magnet motor, dual solenoid service and emergency disc brakes, mounted at the top of the hoistway.

C. Governor:  The governor shall be a tension type governor.

D. Buffers, Car and Counterweight:  Compression spring type buffers shall be used.

E. Hoistway Operating Devices

1. Emergency stop switch in the pit.

2. Terminal stopping switches.

F. Positioning System:  Consists of an encoder, reader box, and door zone vanes.

G. Guide Rails and Attachments:  Guide rails shall be tee-section steel rails with brackets and fasteners.  Side counterweight arrangements shall have a dual-purpose bracket that combines both counterweight guide rails, and one of the car guide rails to building fastening.

H. Coated Steel Belts:  Polyurethane coated belts with high-tensil-grade, zinc-plated steel cords.

I. Governor Rope:  Governor rope shall be steel and shall consist of at least eight strands wound about a sisal core center.

J. Fascia:  Galvanized sheet steel shall be provided at the front of the hoistway.

K. Carframe and Safety:  A carframe fabricated from formed or structural steel members shall be provided with adequate bracing to support the platform and car enclosures.  The car safety shall be integral to the carframe and shall be Type “B”, flexible guide clamp type.

L. Emergency Car Lighting:  An emergency power unit employing a 6-volt sealed rechargeable battery and totally static circuits shall be provided to illuminate the elevator car and provide current to the alarm bell in the event of building power failure.

M. Emergency Pulsating Sire:  Siren mounted on top of the car that is activated when the alarm button in the car operating panel is engaged.  Siren shall have a rated sound pressure level of 80 dB(A) at a distance of 3.0 m from the device.  Siren shall respond with a delay of not more than 1 second after the switch or push button has been pressed.

N. Fan:  A two speed 120 VAC fan shall be mounted to the structural ceiling to facilitate in-car air circulation, meeting A17.1 code requirements.  This two-speed fan shall produce airflow rates of 7.2 and 9.2 m3/min on low and high setting, respectively.  The fan shall be rubber mounted to prevent the transmission of structural vibration and shall include a baffle to diffuse audible noise.  A swith shall be provided in the car-operating panel to control the fan.

O. Emergency Exit Contact:  An electrical contact shall be provded on the car-top exit.

P. Roller Guides:  Rubber roller guides shall be mounted on the top and the bottom of the car and counterweight.  Car roller guides shall be 6-1/4” (160 mm) at the top and bottom of the car.  The counterweight roller guides shall be 3” (76 mm) at the top and the bottom.
Q. Platform:  The car platform shall be constructed of 2 layers of plywood and 2 layers of .032-inch (.81 mm) thick aluminum laminate for a total thickness of 1-1/2 inches (38 mm).  Load weighing device shall be mouned under the platform. 

2.3 OPERATION SYSTEMS

A. General:  Provide manufacturer's standard microprocessor operation system as required to provide type of operation system indicated.

B. Controller Location:  Controller shall be located adjacent to the hoistway at the top landing in a controller space or a control room.

Retain paragraph and one of two subparagraphs below for cars that are not in groups, if applicable.  If only one elevator is required, delete option in paragraph title.

C. Auxiliary Operations:

Typical operational features are described in subparagraphs below.

Caution:  There are many possible definitions of standby (emergency) power operation.  Subparagraphs below are examples only; coordinate with Division 26 Sections and ensure that what is to be provided is clear both here and in Division 26.

1. Standby Power Operation:  On activation of standby power, car is returned to a designated floor and parked with doors open.  Car can be manually put in service on standby power, either for return operation or for regular operation, by switches in control panel.

2. Battery-Powered Lowering:  If power fails and car is at a floor, it remains at that floor, opens its doors, and shuts down.  If car is between floors, it is lowered to the next floor below, opens its doors, and shuts down.  System includes rechargeable battery and automatic recharging system.

D. Security Feature:  Security feature shall not affect emergency firefighters' service.

1. Card-Reader Operation:  System uses card readers at car control stations to authorize calls.  Security system determines which landings and at what times calls require authorization by card reader.  Allow space as indicated for card reader in car.

a. Security access system equipment as required by LARNG.

2.4 DOOR REOPENING DEVICES

A. Infrared Array:  Provide door reopening devices with uniform array of 36 or more microprocessor-controlled, infrared light beams projecting across car entrance.  Interruption of one or more of the light beams shall cause doors to stop and reopen.

Generally retain paragraph below to minimize elevator delay; feature may be unnecessary for low-rise elevators.

B. Nudging Feature:  After car doors are prevented from closing for predetermined adjustable time, a loud buzzer shall sound and doors shall begin to close at reduced kinetic energy.

2.5 FINISH MATERIALS

A. Cold-Rolled Steel Sheet:  ASTM A 1008/A 1008M, commercial steel, Type B, exposed.

B. Hot-Rolled Steel Sheet:  ASTM A 1011/A 1011M, commercial steel, Type B, pickled.

C. Stainless-Steel Sheet:  ASTM A 240/A 240M, Type 304.

D. Stainless-Steel Bars:  ASTM A 276, Type 304.

Retain paragraph above or first paragraph below, or both if needed for handrails.

E. Stainless-Steel Tubing:  ASTM A 554, Grade MT 304.

F. Aluminum Extrusions:  ASTM B 221 (ASTM B 221M), Alloy 6063.

2.6 CAR ENCLOSURES

Removable wall panels allow panels to be replaced with little downtime and allow car, with finished wall panels removed, to be used during construction.  Cars with nonremovable panels are less expensive.

A. General:  Provide  steel-framed car enclosures with nonremovable wall panels, with car roof, access doors, power door operators, and ventilation.

1. Provide standard railings complying with ASME A17.1 on car tops where required by ASME A17.1.

2. Stainless-Steel Wall Panels:  Flush, hollow-metal construction.

3. Stainless-Steel Doors:  Flush, hollow-metal construction.

4. Sills:  Extruded aluminum, with grooved surface, 1/4 inch (6.4 mm) thick.

5. Luminous Ceiling:  Fluorescent light fixtures and ceiling panels of translucent acrylic or other permanent rigid plastic.

2.7 HOISTWAY ENTRANCES

A. General:  Provide manufacturer's standard horizontal-sliding, door-and-frame hoistway entrances complete with track systems, hardware, sills, and accessories.

Delete subparagraph below if no gypsum board shaft walls.

1. Where gypsum board wall construction is indicated, provide self-supporting frames with reinforced head sections.

B. Materials and Fabrication:  Provide manufacturer's standards, but not less than the following:

Delete subparagraphs below not required; revise or add additional items to suit Project.

1. Stainless-Steel Frames:  Formed from stainless-steel sheet.

2. Stainless-Steel Doors:  Flush, hollow-metal construction.

3. Sills:  Extruded aluminum, with grooved surface, 1/4 inch (6.4 mm) thick.

Retain subparagraph below for grouting door sills.

4. Nonshrink, Nonmetallic Grout:  Factory-packaged, nonstaining, noncorrosive, nongaseous grout complying with ASTM C 1107.

2.8 SIGNAL EQUIPMENT

A. General:  Provide hall-call and car-call buttons that light when activated and remain lit until call has been fulfilled.  Fabricate lighted elements with long-life incandescent lamps and acrylic or other permanent, nonyellowing translucent plastic diffusers or LEDs.

B. Car Control Stations:  Provide manufacturer's standard car control stations.  Mount in return panel adjacent to car door, unless otherwise indicated.

C. Emergency Communication System:  Provide system that complies with ASME A17.1 and the U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG)." On activation, system dials preprogrammed number of monitoring station and identifies elevator location to monitoring station.  System provides two-way voice communication without using a handset and provides visible signals that indicate when system has been activated and when monitoring station has responded.  System is contained in flush-mounted cabinet, with identification, instructions for use, and battery backup power supply.

Retain first paragraph below where required by building code.

D. Firefighters' Two-Way Telephone Communication Service:  Provide flush-mounted cabinet  in each car and required conductors in traveling cable for firefighters' two-way telephone communication service specified in Division 28 Section "Fire Detection and Alarm."

E. Car Position Indicator:  Provide illuminated,  digital-type car position indicator, located above car door or above car control station.  Also provide audible signal to indicate to passengers that car is either stopping at or passing each of the floors served.

1. Include travel direction arrows if not provided in car control station.

F. Hall Push-Button Stations:  Provide hall push-button stations at each landing as indicated.

G. Hall Lanterns:  Units with illuminated arrows.

Retain one of two subparagraphs below.

1. Units mounted in both jambs of entrance frame.

H. Hall Annunciator:  With each hall lantern, provide audible signals indicating car arrival and direction of travel.  Signals sound once for up and twice for down.

Delete paragraph below if signs are specified in another Section.

I. Corridor Call Station Pictograph Signs:  Provide signs matching hall push-button stations, with text and graphics as required by authorities having jurisdiction.

2.9 ELEVATORS

Copy and edit paragraph and subparagraphs below for each elevator or group of elevators required.

A. Elevator Description:

1. Machine Location:  Hoistway; no machine room is provided.

Usually delete subparagraph below if net platform size is shown on Drawings or if inside-car dimensions are included in "Car Enclosures" Subparagraph.

2. Rated Load:  4000 lb (1816 kg).

Delete first subparagraph below if no service elevators.

3. Freight Loading Class for Service Elevator(s):  Class A.

4. Rated Speed:  200 fpm (1.0 m/s). 

Retain applicable operation system in first subparagraph below.  First option is for single elevator.  Second option is basic group operation suitable for two or possibly three elevators.  Third option is usually best choice for three or more elevators.

5. Operation System:  Selective collective automatic operation.

6. Auxiliary Operations:

a. Standby power operation.

b. Battery-powered lowering.

c. Automatic dispatching of loaded car.

d. Nuisance call cancel.

7. Car Enclosures:

a. Inside Width:  68 inches (1727 mm) from side wall to side wall.

Before retaining options in subparagraph above and first subparagraph below, verify that selected configuration complies with requirements for providing accessibility to people with disabilities and to emergency stretchers.  Revise descriptions of width and depth if car has more than one entrance.

b. Inside Depth:  90 inches (2286 mm) from back wall to front wall (return panels).

c. Inside Height:  94 inches (2388 mm) to underside of ceiling.

d. Front Walls (Return Panels):  Satin stainless steel, No. 4 finish.

e. Car Fixtures:  Polished stainless steel, No. 8 finish.

f. Side and Rear Wall Panels:  Satin stainless steel, No. 4 finish.

Plastic-laminate doors are about as expensive as stainless-steel doors but are not as durable.

g. Door Faces (Interior):  Satin stainless steel, No. 4 finish.

h. Handrails:  1-1/2 inches (38 mm) round or 1/2 by 2 inches (13 by 50 mm) rectangular  satin stainless steel, No. 4 finish, at sides and rear of car.

i. Floor prepared to receive resilient tile (specified in Division 09 Section "Resilient Flooring").

8. Hoistway Entrances:  As follows:

a. Width:  42 inches (1067 mm).

b. Height:  84 inches (2134 mm) .

c. Type:  Two-speed center opening.

Delete subparagraph below if not applicable, such as for elevators that are not within a fire-rated shaft.  Delete temperature-rise rating if not required.

d. Fire-Protection Rating:  1-1/2 hours.

Copy and edit subparagraph below to suit Project.

e. Frames:  Satin stainless steel, No. 4 finish.

Copy and edit subparagraph below to suit Project.  Plastic-laminate doors are about as expensive as stainless-steel doors but are not as durable.

f. Doors:  Satin stainless steel, No. 4 finish.

Copy and edit first subparagraph below to suit Project.

9. Hall Fixtures:  Satin stainless steel, No. 4 finish.

10. Additional Requirements:

a. Provide inspection certificate in each car, mounted under acrylic cover with frame made from polished stainless steel, No. 8 finish.

Delete subparagraph below if not required.

b. Provide blanket hooks and one complete set(s) of full-height protective blankets.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Sound Isolation:  Mount rotating and vibrating equipment on vibration-isolating mounts designed to minimize transmission of vibrations to structure and thereby minimize structure-borne noise from elevator system.

B. Leveling Tolerance:  1/8 inch (3 mm), up or down, regardless of load and direction of travel.

C. Set sills flush with finished floor surface at landing.  Fill space under sill solidly with nonshrink, nonmetallic grout.

3.2 FIELD QUALITY CONTROL

A. Acceptance Testing:  On completion of elevator installation and before permitting use (either temporary or permanent), perform acceptance tests as required and recommended by ASME A17.1 and by governing regulations and agencies.

3.3 PROTECTION

A. Temporary Use: Comply with the following requirements for elevator used for construction purposes:

1. Provide car with temporary enclosure, either within finished car or in place of finished car, to protect finishes from damage.

2. Provide other protective coverings, barriers, devices, signs, and procedures as needed to protect elevator and elevator equipment.

3. Engage elevator Installer to provide full maintenance service.

4. Engage elevator Installer to restore damaged work, if any, so no evidence remains of correction.  Return items that cannot be refinished in the field to the shop, make required repairs and refinish entire unit, or provide new units as required.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to operate, adjust, and maintain elevator(s).  

END OF SECTION 14210


ELECTRIC TRACTION ELEVATORS

14210 - 7

