Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


Copyright 2000, The American Institute of Architects (AIA)

SECTION 16750 - VOICE AND DATA COMMUNICATION CABLING

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 – GENERAL
1.1
RELATED DOCUMENTS
A.
Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2
SUMMARY

A.
This Section includes wire, cable, connecting devices, installation, and testing for wiring systems to be used as signal pathways for voice and high-speed data transmission.

1.3
DEFINITIONS

Retain acronyms and abbreviations that remain after this Section has been edited.

A.
EMI:  Electromagnetic interference.

B.
IDC:  Insulation displacement connector.

C.
LAN:  Local area network.

D.
PVC:  Polyvinyl chloride.

E.
STP:  Shielded twisted pair.

F.
UTP:  Unshielded twisted pair.

1.4
SUBMITTALS

A.
Product Data:  Include data on features, ratings, and performance for each component specified.

B.
Shop Drawings:  Include dimensioned plan and elevation views of each individual component.  Show equipment assemblies, method of field assembly, workspace requirements, and access for cable connections.

1.
System labeling schedules, including electronic copy of labeling schedules, as specified in Part 3, in software and format selected by Owner.

2.
Wiring diagrams.  Show typical wiring schematics including the following:

Edit subparagraphs below to suit Project.

a.
Workstation outlets, jacks, and jack assemblies.

b.
Patch cords.

c.
Patch panels.

d.
Fiber-optic boxes.

C.
Cable Administration Drawings:  As specified in Part 3.

Retain first paragraph below when workstation outlet faceplates have critical features needing hands-on appraisal.

D.
Samples:  For workstation outlets, jacks, jack assemblies, and faceplates for color selection and evaluation of technical features.

E.
Product Certificates:  For each type of cable, connector, and terminal equipment, signed by product manufacturer.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Seismic Controls for Electrical Work."  Delete if all cross-connect and patch panels are mounted on backboards.

F.
Manufacturer Seismic Qualification Certification:  Submit certification that distribution racks and their components will withstand seismic forces defined in Division 16 Section "Seismic Controls for Electrical Work."  Include the following:

1.
Basis for Certification:  Base certification on the maximum number of components capable of being mounted in each rack type.  Identify components on which certification is based.  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a.
The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b.
The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2.
Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity of each rack-mounted component and of each assembled rack type, and locate and describe mounting and anchorage provisions.

3.
Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

G.
Qualification Data:  For Installer.

Delete first paragraph below if Owner engages an independent testing agency to perform field quality-control testing.

H.
Field quality-control test reports.

I.
Operation and Maintenance Data:  For voice and data communication cabling to include in emergency, operation, and maintenance manuals.

1.5
QUALITY ASSURANCE

Association in paragraph below is an industry trade association.  See Editing Instruction No. 2 in the Evaluations.

A.
Installer Qualifications:  System installer must have on staff a registered communication distribution designer certified by Building Industry Consulting Service International.

Retain first paragraph and subparagraph below if Contractor selects testing agency.  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

B.
Testing Agency Qualifications:  An independent testing agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1.
Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

C.
Source Limitations:  Obtain all products through one source from a single manufacturer.

D.
Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E.
Comply with NFPA 70.

1.6
COORDINATION

Revise this Article to specify coordination with other parties involved in finalizing voice and data communication cabling.  See Editing Instruction No. 3 in the Evaluations.

A.
Coordinate layout and installation of voice and data communication cabling with Owner's telecommunications and LAN equipment suppliers.  Coordinate service entrance arrangement with local exchange carrier.

1.
Meet jointly with telecommunications and LAN equipment suppliers, local exchange carrier representatives, and Owner to exchange information and agree on details of equipment arrangements and installation interfaces.

2.
Record agreements reached in meetings and distribute to other participants.

3.
Adjust arrangements and locations of distribution frames and cross-connect and patch panels in equipment rooms and wiring closets to accommodate and optimize arrangement and space requirements of telephone switch and LAN equipment.

1.7
EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A.
Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise first subparagraph below to suit Project.

1.
Cable:  250 feet (76 m) of each size and type used for Project.  Furnish on reels.

2.
Patch-Panel Units:  One of each type for every six installed, but no fewer than one.

3.
Connecting Blocks:  One of each type for every 25 installed, but no fewer than one.

4.
Outlet Assemblies:  One of each type for every 25 installed, but no fewer than one.

PART 2 - PRODUCTS

2.1
MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A.
Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B.
Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1.
Cable:

a.
Belden Inc.; Electronics Division.

b.
Berk-Tek; an Alcatel Company.

c.
Brand-Rex Co.; Unit of BICC Cables Corp.

d.
Champlain Cable Corporation.

e.
Chromatic Technologies, Incorporated.

f.
General Cable Corporation.

g.
HeLix/HiTemp Cables, Inc.

h.
ICC.

i.
Lucent Technologies; Global Service Provider.

j.
Mohawk/CDT; a division of Cable Design Technologies.

k.
Montrose/CDT; a division of Cable Design Technologies.

l.
Optical Cable Corporation.

m.
Panduit Corp.

n.
Prestolite Wire Corp.

o.
Remee Products Corp.

p.
Siecor.

q.
Superior Essex; Superior Telecommunications Inc.

2.
Terminal and Connector Components and Distribution Racks:

a.
AMP Incorporated; a Tyco International Ltd. Company.

b.
Hubbell Premise Wiring.

c.
Leviton Telecom.

d.
Lucent Technologies; Global Service Provider.

e.
Panduit Corp.

f.
Thomas & Betts Corporation.

2.2
SYSTEM REQUIREMENTS

A.
General:  Coordinate the features of materials and equipment so they form an integrated system.  Match components and interconnections for optimum future performance.

Revise percentage below to suit Project.

B.
Expansion Capability:  Unless otherwise indicated, provide spare fibers and conductor pairs in cables, positions in cross-connect and patch panels, and terminal strips to accommodate 20 percent future increase in active workstations.

2.3
MOUNTING ELEMENTS

A.
Cable Trays:  Comply with Division 16 Section "Cable Trays."

B.
Raceways and Boxes:  Comply with Division 16 Section "Raceways and Boxes."

C.
Backboards:  3/4-inch (19-mm), interior-grade, fire-retardant-treated plywood.

Delete paragraph below if all cross-connect and patch panels are mounted on backboards.  Coordinate with Drawings.

D.
Distribution Racks:  Freestanding and wall-mounting, modular-steel units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

Revise dimensions in first subparagraph below to suit Project or delete and indicate on Drawings.

1.
Approximate Module Dimensions:  84 inches (2130 mm) high by 22 inches (560 mm) wide.

2.
Finish:  Baked-polyester powder coat.

2.4
TWISTED-PAIR CABLES, CONNECTORS, AND TERMINAL EQUIPMENT

Revise category numbers in first paragraph below to coordinate with Part 3 "Application of Media" Article.

A.
Cables:  Listed as complying with Category 6 of TIA/EIA-568-A.

B.
Conductors:  Solid copper.

Select UTP or STP cable and connecting hardware in remaining paragraphs and subparagraphs below to suit Project.

C.
UTP Cable:  Comply with TIA/EIA-568-A.  Four, thermoplastic-insulated, individually twisted pairs of conductors; No. 24 AWG, color-coded; enclosed in PVC jacket.

D.
STP Workstation Cable:  Comply with TIA/EIA-568-A.  Two, thermoplastic-insulated, individually twisted pairs of conductors; No. 22 AWG, color-coded, overall aluminum and polyester shield and No. 22 AWG, tinned-copper drain wire; enclosed in PVC jacket.

E.
UTP and STP Plenum Cable:  Listed for use in air-handling spaces.  Features are as specified for cables, conductors, UTP cable, and STP workstation cable except materials are modified as required for listing.

Several types of IDCs below are in common use.  See Editing Instruction No. 4 in the Evaluations.  Coordinate with Drawings.

F.
UTP Cable Connecting Hardware:  Comply with TIA/EIA-568-A.  IDC type, using modules designed for punch-down caps or tools.

1.
IDC Terminal Block Modules:  Integral with connector bodies, including plugs and jacks where indicated.

2.
IDC Connecting Hardware:  Consistent throughout Project.

G.
STP Cable Connecting Hardware:  Comply with TIA/EIA-568-A for connectors, plugs, and jack assemblies.

Delete paragraph below if cross connection is accomplished exclusively on patch panels.  Coordinate with Drawings.

H.
Cross-Connect Panel:  Modular array of IDC terminal blocks arranged to terminate building cables and permit interconnection between cables.  
Revise quantity in first subparagraph below to suit Project.

1.
Number of Terminals per Field:  One for each conductor in assigned cables.

2.
Mounting:  Backboard.

I.
Patch Panel:  Modular panels housing multiple-numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.  Panels shall have punch downs on the back and RJ45 connectors on the front.  All 8 wires per cable shall be punched down.
Select number of jacks per field from options in first subparagraph below.  Coordinate with Drawings for quantity of fields.

1.
Number of Jacks per Field:  One for each four-pair conductor group of indicated cables, plus spares and blank positions adequate to satisfy specified expansion criteria.
2.
Mounting:  Rack.
Revise first two paragraphs below if other than RJ-45 modular connectors are required for some applications.  See Editing Instruction No. 5 in the Evaluations.

J.
Jacks and Jack Assemblies for UTP Cable:  Modular, color-coded, RJ-45 receptacle units with integral IDC-type terminals.  Use keyed jacks for data service.

K.
UTP Patch Cords:  Four-pair cables in 48-inch (1200-mm) lengths, terminated with RJ-45 plug at each end.  Use keyed plugs for data service.

L.
STP Patch Cords:  Two-pair cables in 48-inch (1200-mm) lengths, terminated with STP plug connectors at both ends.  Match plug connectors with patch-panel connectors.

Edit below to suit Project.  Coordinate with other items specified to be mounted in workstation faceplates.  Coordinate with Drawings.

M.
Workstation Outlets:  Quad or Octal jack-connector assemblies mounted in single or multigang faceplate.

1.
Faceplate:  High-impact plastic; color as selected by Architect.

2.
Mounting:  Flush, unless otherwise indicated.

3.
Legend:  Factory labeled, top jack "Voice" and bottom jack "Data," by silk-screening or engraving.

2.5
FIBER-OPTIC CABLES, CONNECTORS, AND TERMINAL EQUIPMENT

A.
Cables:  Factory fabricated, jacketed, low loss, glass type, fiber optic, multimode, graded index, operating at 850 and 1300 nm.

1.
Workstation, Strands per Cable:  Two.

2.
Backbone, Strands per Cable:  12, unless otherwise indicated.

3.
Dimensions:  62.5-micrometer core diameter; 125-micrometer cladding diameter.

4.
Maximum Attenuation:  Minus 3.75 dB/km at 850 nm; minus 1.5 dB/km at 1300 nm.

5.
Minimum Modal Bandwidth:  160 MHz/km at 850 nm; 500 MHz/km at 1300 nm.

6.
Operating Temperature Range:  Minus 20 to plus 70 deg C.

B.
Plenum Cable:  Listed for use in plenums.

C.
Cable Connectors:  Quick-connect, simplex- and duplex-type SC couplers with self-centering, axial alignment mechanisms.  Insertion loss not more than 0.7 dB.

D.
Patch Panel:  Modular panels housing multiple-numbered, duplex cable connectors.

1.
Permanent Connection:  Permanently connect one end of each connector module to installed cable fiber.

Coordinate first subparagraph below with Drawings.

2.
Number of Connectors per Field:  One for each fiber of cable or cables assigned to field, plus spares and blank positions adequate to satisfy specified expansion criteria.

3.
Mounting:  Backboard or Rack.
E.
Patch Cords:  Dual fiber cables in 36-inch (900-mm) lengths.

1.
Terminations:  Two duplex connectors arranged to mate with patch-panel connectors, one at each end of each fiber in cord.

Delete below or edit to suit Project.  Coordinate with other items specified to be mounted in workstation faceplates.  Edit to be compatible with plug-and-jack type specified for telephone service.  Coordinate with Drawings.  See Editing Instruction No. 5 in the Evaluations.

F.
Workstation Outlets:  Flush dual fiber-optic connector assemblies mounted in two-gang faceplate with flush dual RJ-45 jack assembly.

1.
Faceplate:  High-impact plastic; color as selected by Architect.

2.
Mounting:  Flush, unless otherwise indicated.

3.
Legend:  Factory labeled, fiber-optic connectors "Data" and RJ-45 jacks "Voice," by engraving.

2.6
IDENTIFICATION PRODUCTS

Select appropriate Section from options in paragraph below.

A.
Comply with Division 16 Section Electrical Identification and the following:

Retain below with either option selected in paragraph above.

1.
Cable Labels:  Self-adhesive vinyl or vinyl-cloth wraparound tape markers, machine printed with alphanumeric cable designations.

PART 3 - EXECUTION

3.1
EXAMINATION

A.
Examine pathway elements intended for cables.  Check raceways, cable trays, and other elements for compliance with space allocations, installation tolerances, hazards to cable installation, and other conditions affecting installation.  Proceed with installation only after unsatisfactory conditions have been corrected.

3.2
APPLICATION OF MEDIA

Edit this Article to suit Project.  Select data backbone media from options in paragraph below.

A.
Backbone Cable for Data Service:  Use fiber-optic cable for runs between equipment rooms and wiring closets and for runs between wiring closets.

Select voice backbone media from options in paragraph below.

B.
Backbone Cable for Voice Service:  Use UTP Category  6 cable for runs between equipment rooms and wiring closets and for runs between wiring closets.

Select data horizontal media from options in paragraph below.

C.
Horizontal Cable for Data Service:  Use UTP Category 6 cable for runs between wiring closets and workstation outlets.

Select voice horizontal media from options below.

D.
Horizontal Cable for Voice Service:  Use UTP Category  6 cable for runs between wiring closets and workstation outlets.

3.3
INSTALLATION

Select one of two paragraphs below and edit to suit Project.

A.
Wiring Method:  Install wiring and optical fiber in raceway and cable tray except within consoles, cabinets, desks, and counters.  Conceal raceway and wiring except in unfinished spaces.

B.
Install cables using techniques, practices, and methods that are consistent with Category  6 rating of components and that ensure Category  6 performance of completed and linked signal paths, end to end.

C.
Install cables without damaging conductors, shield, or jacket.

D.
Do not bend cables, in handling or in installing, to smaller radii than minimums recommended by manufacturer.

E.
Pull cables without exceeding cable manufacturer's recommended pulling tensions.

1.
Pull cables simultaneously if more than one is being installed in same raceway.

2.
Use pulling compound or lubricant if necessary.  Use compounds that will not damage conductor or insulation.

3.
Use pulling means, including fish tape, cable, rope, and basket-weave wire or cable grips, that will not damage media or raceway.

F.
Install exposed cables parallel and perpendicular to surfaces or exposed structural members and follow surface contours where possible.

H.
Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

I.
Wiring within Wiring Closets and Enclosures:  Provide conductors of adequate length.  Train conductors to terminal points with no excess.  Use lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

J.
Separation of Wires:  Comply with TIA/EIA-569-A rules for separating unshielded copper voice and data communication cabling from potential EMI sources, including electrical power lines and equipment.

K.
Make splices, taps, and terminations only at indicated outlets, terminals, and cross-connect and patch panels.

L.
Use splice and tap connectors compatible with media types.

3.4
GROUNDING

Revise this Article to suit Project.  Coordinate with Drawings.

A.
Comply with Division 16 Section "Grounding and Bonding."

B.
Ground cable shields, drain conductors, and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

For considerations about bonding shields to ground in first paragraph below, see Editing Instruction No. 6 in the Evaluations.

C.
Bond shields and drain conductors to ground at only one point in each circuit.

D.
Signal Ground Terminal:  Locate in each equipment room and wiring closet; isolate from power system and equipment grounding.

E.
Signal Ground Bus:  Mount on wall of main equipment room with standoff insulators.

F.
Signal Ground Backbone Cable:  Extend from signal ground bus to signal ground terminal in each equipment room and wiring closet.

3.5
INSTALLATION IN EQUIPMENT ROOMS AND WIRING CLOSETS

Coordinate this Article with Drawings.

A.
Install plywood backboards on walls of equipment rooms and wiring closets from floor to ceiling.

B.
Mount patch panels, terminal strips, and other connecting hardware on backboards, unless otherwise indicated.

C.
Group connecting hardware for cables into separate logical fields.

D.
Use patch panels to terminate cables entering the space, unless otherwise indicated.

3.6
INSTALLATION STANDARDS

A.
Comply with requirements in TIA/EIA-568-A and TIA/EIA-569-A.

3.7
IDENTIFICATION

Select appropriate Section from options in first paragraph below.

A.
In addition to requirements in this Article, comply with applicable requirements in Division 16 Section Electrical Identification and TIA/EIA-606.

B.
System:  Use a unique, three-syllable, alphanumeric designation for each cable, and label cable and jacks, connectors, and terminals to which it connects with same designation.  Use logical and systematic designations for facility's architectural arrangement.

1.
First syllable identifies and locates equipment room or wiring closet where cables originate.

2.
Second syllable identifies and locates cross-connect- or patch-panel field in which cables terminate.

3.
Third syllable designates type of media (copper or fiber) and position occupied by cable pairs or fibers in field.

C.
Workstation:  Label cables within outlet boxes.

D.
Distribution Racks and Frames:  Label each unit and field within that unit.

E.
Within Connector Fields in Equipment Rooms and Wiring Closets:  Label each connector and each discrete unit of cable-terminating and connecting hardware.  Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

F.
Cables, General:  Label each cable within 4 inches (100 mm) of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

G.
Exposed Cables and Cables in Cable Trays and Wire Troughs:  Label each cable at intervals not exceeding 15 feet (4.5 m).

H.
Cable Schedule:  Post in prominent location in each equipment room and wiring closet.  List incoming and outgoing cables and their designations, origins, and destinations.  Protect with rigid frame and clear plastic cover.  Furnish an electronic copy of final comprehensive schedules for Project, in software and format selected by Owner.

I.
Cable Administration Drawings:  Show building floor plans with cable administration point labeling.  Identify labeling convention and show labels for telecommunications closets, backbone pathways and cables, entrance pathways and cables, terminal hardware and positions, horizontal cables, work areas and workstation terminal positions, grounding buses and pathways, and equipment grounding conductors.  Follow convention of TIA/EIA-606.  Furnish electronic record of all drawings, in software and format selected by Owner.

3.8
FIELD QUALITY CONTROL

Retain one of three paragraphs below.

A.
Testing Agency:  Engage a qualified testing and inspecting agency to perform the following field tests and inspections and prepare test reports:

B.
Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with either of last two paragraphs selected above.  Edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.

1.
Operational Test:  After installation of cables and connectors, demonstrate product capability and compliance with requirements.  Test each signal path for end-to-end performance from each end of all pairs installed.  Remove temporary connections when tests have been satisfactorily completed.

2.
Copper Cable Procedures:  Inspect for physical damage and test each conductor signal path for continuity and shorts.  Use Class 2, bidirectional, Category 5 tester.  Test for faulty connectors, splices, and terminations.  Test according to TIA/EIA-TSB67, "Transmission Performance Specifications for Field Testing of Unshielded Twisted-Pair Cabling Systems." Link performance for UTP cables must meet minimum criteria of TIA/EIA-568-A.

Referenced tests in NETA ATS include inspection procedures to verify physical condition and tests and measurements to verify proper installation.

3.
Fiber-Optic Cable Procedures:  Perform each visual and mechanical inspection and electrical test, including optional procedures, stated in NETA ATS, Section 7.25.  Certify compliance with test parameters and manufacturer's written recommendations.  Test optical performance with optical power meter capable of generating light at all appropriate wavelengths.

C.
Remove malfunctioning units, replace with new units, and retest as specified above.

3.9
DEMONSTRATION

A.
Train Owner's maintenance personnel in cable-plant management operations, including changing signal pathways for different workstations, rerouting signals in failed cables, and extending wiring to establish new workstation outlets.  

END OF SECTION 16750

VOICE AND DATA COMMUNICATION CABLING

16750 - 10

