Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana
                                                           Technical specifications


SECTION 15350 – COMMISSIONING

PART 1 - GENERAL

1.1
DESCRIPTION


A.
The purpose of this section is to specify Division 15 responsibilities in the commissioning process of the Design Build Contractor.

B.
The systems to be commissioned are as follows (See system checklists in Part 3):


1. Chilled Water System



2. Condenser Water System



3. Heating System



4. Air Distribution Systems



5. Building Automation System



6. Exhaust Systems



7. Plumbing Systems



8. Domestic Water Heating Systems



9. Piping Systems


C.
Commissioning requires the participation of Division 15 to ensure that all systems are operating in a manner consistent with the Contract Documents. Division 15 shall be familiar with all parts of the commissioning plan issued by the Commissioning Agent (CA) and shall execute all commissioning responsibilities assigned to them in the Contract Documents.

1.2
RESPONSIBILITIES


A.
The commissioning responsibilities applicable to each of the mechanical, controls and TAB contractors of Division 15 are as follows (all references apply to commissioned equipment only):


B.
Construction and Acceptance Phases



1.
Include and itemize the cost of commissioning in the contract price.



2.
In each purchase order or subcontract written, include requirements for submittal data, commissioning documentation, O&M data and training.



3.
Attend a commissioning scoping meeting and other meetings necessary to facilitate the commissioing process.



4.
Contractors shall provide the CA with normal cut sheets and shop drawing submittals of commissioned equipment.



5.
Provide additional requested documentation, prior to normal O&M manual submittals, to the CA for development of start-up and functional testing procedures. 




a.
Typically this will include detailed manufacturer installation and start-up, operating, troubleshooting and maintenance procedures, full details of any owner-contracted tests, fan and pump curves, full factory testing reports, if any, and full warranty information, including all responsibilities of the Owner to keep the warranty in force clearly identified.  In addition, the installation, start-up and checkout materials that are actually shipped inside the equipment and the actual field checkout sheet forms to be used by the factory or field technicians shall be submitted to the Commissioning Agent.  




b.
The Commissioning Agent may request further documentation necessary for the commissioning process.




c.
This data request may be made prior to normal submittals.



6.
Provide a copy of the O&M manuals and submittals of commissioned equipment, through normal channels, to the CA for review and approval.



7.
Contractors shall assist (along with the design engineers) in clarifying the operation and control of commissioned equipment in areas where the specifications, control drawings or equipment documentation is not sufficient for writing detailed testing procedures.



8.
Provide limited assistance to the CA in preparing the specific functional performance test procedures as specified.  Subs shall review test procedures to ensure feasibility, safety and equipment protection and provide necessary written alarm limits to be used during the tests.



9.
Develop a full start-up and initial checkout plan using manufacturer’s start-up procedures and the prefunctional checklists from the CA for all commissioned equipment.  Submit to CA for review and approval prior to startup.  



10.
During the startup and initial checkout process, execute the mechanical-related portions of the prefunctional checklists for all commissioned equipment.



11.
Perform and clearly document all completed startup and system operational checkout procedures, providing a copy to the CA.



12.
Address current A/E punch list items before functional testing.  Air and water TAB shall be completed with discrepancies and problems remedied before functional testing of the respective air- or water-related systems.



13.
Provide skilled technicians to execute starting of equipment and to execute the functional performance tests.  Ensure that they are available and present during the agreed upon schedules and for sufficient duration to complete the necessary tests, adjustments and problem-solving.



14.
Provide skilled technicians to perform functional performance testing under the direction of the CA for specified equipment.  Assist the CA in interpreting the monitoring data, as necessary.



15.
Correct deficiencies (differences between specified and observed performance) as interpreted by the CA, CM and A/E and retest the equipment.



16.
Prepare O&M manuals according to the Contract Documents, including clarifying and updating the original sequences of operation to as-built conditions.



17.
During construction, maintain as-built red-line drawings for all drawings and final CAD as-builts for contractor-generated coordination drawings. Update after completion of commissioning (excluding deferred testing).



18.
Provide training of the Owner’s operating staff using expert qualified personnel, as specified.



19.
Coordinate with equipment manufacturers to determine specific requirements to maintain the validity of the warranty.

C.
Warranty Period



1.
Execute seasonal or deferred functional performance testing, witnessed by the CA, according to the specifications.



2.
Correct deficiencies and make necessary adjustments to O&M manuals and as-built drawings for applicable issues identified in any seasonal testing.


B.
The responsibilities of the HVAC Mechanical Contractor, during construction and acceptance phases in addition to those listed in (A) are:



1.
Provide startup for all HVAC equipment, except for the building automation control system.



2.
Assist and cooperate with the TAB contractor and CA by:




a.
Putting all HVAC equipment and systems into operation and continuing the operation during each working day of TAB and commissioning, as required.




b.
Including cost of sheaves and belts that may be required by TAB.




c.
Providing test holes in ducts and plenums where directed by TAB to allow air measurements and air balancing.  Providing an approved plug.




d.
Providing temperature and pressure taps according to the Construction Documents for TAB and commissioning testing.



3.
Install a P/T plug at each water sensor which is an input point to the control system.



4.
List and clearly identify on the as-built drawings the locations of all air-flow stations.



5.
Prepare a preliminary schedule for Division 15 pipe and duct system testing, flushing and cleaning, equipment start-up and TAB start and completion for use by the CA.  Update the schedule as appropriate.



6.
Notify the CA when pipe and duct system testing, flushing, cleaning, startup of each piece of equipment and TAB will occur.  Be responsible to notify the CA, ahead of time, when commissioning activities not yet performed or not yet scheduled will delay construction.  Be proactive in seeing that commissioning processes are executed and that the CA has the scheduling information needed to efficiently execute the commissioning process.

D.
The commissioning responsibilities of the Controls Contractor, during construction and acceptance phases in addition to those listed in (A) are:



1.
The Controls Contractor’s submittals of control drawings shall include complete detailed sequences of operation for each piece of equipment, regardless of the completeness and clarity of the sequences in the specifications.  They shall include:




a.
An overview narrative of the system (1 or 2 paragraphs) generally describing its purpose, components and function.




b.
All interactions and interlocks with other systems.




c.
Detailed delineation of control between any packaged controls and the building automation system, listing what points the BAS monitors only and what BAS points are control points and are adjustable.




d.
Written sequences of control for packaged controlled equipment.  (Equipment manufacturers’ stock sequences may be included, but will generally require additional narrative).




e.
Start-up sequences.




f.
Warm-up mode sequences.




g.
Normal operating mode sequences.




h.
Unoccupied mode sequences.




i.
Shutdown sequences.




j.
Capacity control sequences and equipment staging.




k.
Temperature and pressure control:  setbacks, setups, resets, etc.




l.
Detailed sequences for all control strategies, e.g.,  economizer control, optimum start/stop, staging, optimization, demand limiting, etc.




m.
Effects of power or equipment failure with all standby component functions.




n.
Sequences for all alarms and emergency shut downs.




o.
Seasonal operational differences and recommendations.




p.
Initial and recommended values for all adjustable settings, setpoints and parameters that are typically set or adjusted by operating staff; and any other control settings or fixed values, delays, etc. that will be useful during testing and operating the equipment.




q.
Schedules, if known.




r.
To facilitate referencing in testing procedures, all sequences shall be written in small statements, each with a number for reference.  For a given system, numbers will not repeat for different sequence sections, unless the sections are numbered.



2.
Control Drawings Submittal




a.
The control drawings shall have a key to all abbreviations.




b.
The control drawings shall contain graphic schematic depictions of the systems and each component.




c.
The schematics will include the system and component layout of any equipment that the control system monitors, enables or controls, even if the equipment is primarily controlled by packaged or integral controls.




d.
Provide a full points list with at least the following included for each point:





1)
Controlled system





2)
Point abbreviation





3)
Point description





4)
Display unit





5)
Control point or setpoint (Yes / No)





6)
Monitoring point (Yes / No)





7)
Intermediate point (Yes / No)





8)
Calculated point (Yes / No)






Key:






Point Description: DB temp, airflow, etc.






Control or Setpoint: Point that controls equipment and can have its setpoint changed (OSA, SAT, etc.)






Intermediate Point: Point whose value is used to make a calculation which then controls equipment (space temperatures that are averaged to a virtual point to control reset).






Monitoring Point: Point that does not control or contribute to the control of equipment, but is used for operation, maintenance, or performance verification.






Calculated Point: “Virtual” point generated from calculations of other point values.




e.
The Controls Contractor shall keep the CA informed of all changes to this list during programming and setup.



3.
An updated as-built version of the control drawings and sequences of operation shall be included in the final controls O&M manual submittal.



4.
Assist and cooperate with the TAB contractor in the following manner:




a.
Meet with the TAB contractor prior to beginning TAB and review the TAB plan to determine the capabilities of the control system toward completing TAB.  Provide the TAB any needed unique instruments for setting terminal unit boxes and instruct TAB in  their use (handheld control system interface for use around the building during TAB, etc.).




b.
For a given area, have all required prefunctional checklists, calibrations, startup and selected functional tests of the system completed and approved by the CA prior to TAB.




c.
Provide a qualified technician to operate the controls to assist the TAB contractor in performing TAB, or provide sufficient training for TAB to operate the system without assistance.



5.
Assist and cooperate with the CA in the following manner:




a.
Using a skilled technician who is familiar with this building, execute the functional testing of the controls system as specified. Assist in the functional testing of all equipment specified. Provide two-way radios during the testing.




b.
Execute all control system trend logs specified.



6.
The controls contractor shall prepare a written plan indicating in a step-by-step manner, the procedures that will be followed to test, checkout and adjust the control system prior to functional performance testing.  At minimum, the plan shall include for each type of equipment controlled by the automatic controls:




a.
System name.




b.
List of devices.




c.
Step-by-step procedures for testing each controller after installation, including:





1)
Process of verifying proper hardware and wiring installation.





2)
Process of downloading programs to local controllers and verifying that they are addressed correctly.





3)
Process of performing operational checks of each controlled component.





4)
Plan and process for calibrating valve and damper actuators and all sensors.





5)
A description of the expected field adjustments for transmitters, controllers and control actuators should control responses fall outside of expected values.




d.
A copy of the log and field checkout sheets that will document the process.  This log must include a place for initial and final read values during calibration of each point and clearly indicate when a sensor or controller has “passed” and is operating within the contract parameters.




e.
A description of the instrumentation required for testing.




f.
Indicate what tests on what systems should be completed prior to TAB using the control system for TAB work.  Coordinate with the CA and TAB contractor for this determination.



7.
Provide a signed and dated certification to the CA and CM upon completion of the checkout of each controlled device, equipment and system prior to functional testing for each piece of equipment or system, that all system programming is complete as to all respects of the Contract Documents, except functional testing requirements.



8.
Beyond the control points necessary to execute all documented control sequences, provide monitoring, control and virtual points as specified in Section 15950.



9.
List and clearly identify on the as-built duct and piping drawings the locations of all static and differential pressure sensors (air, water and building pressure).


E.
The duties of the TAB contractor, in addition to those listed in (A) are:



1.
Six weeks prior to starting TAB, submit to the CM the qualifications of the site technician for the project, including the name of the contractors and facility managers of recent projects the technician on which was lead.  The Owner will approve the site technician’s qualifications for this project.



2.
Submit the outline of the TAB plan and approach for each system and component to the CA, CM and the controls contractor six weeks prior to starting the TAB.  This plan will be developed after the TAB has some familiarity with the control system.



3.
The submitted plan will include:




a.
Certification that the TAB contractor has reviewed the construction documents and the systems with the design engineers and contractors to sufficiently understand the design intent for each system.




b.
An explanation of the intended use of the building control system.  The controls contractor will comment on feasibility of the plan.




c.
All field checkout sheets and logs to be used that list each piece of equipment to be tested, adjusted and balanced with the data cells to be gathered for each.




d.
Discussion of what notations and markings will be made on the duct and piping drawings during the process.




e.
Final test report forms to be used.




f.
Detailed step-by-step procedures for TAB work for each system and issue:  terminal flow calibration (for each terminal type), diffuser proportioning, branch / submain proportioning, total flow calculations, rechecking, diversity issues, expected problems and solutions, etc.  Criteria for using air flow straighteners or relocating flow stations and sensors will be discussed.  Provide the analogous explanations for the water side.




g.
List of all air flow, water flow, sound level, system capacity and efficiency measurements to be performed and a description of specific test procedures, parameters, formulas to be used.




h.
Details of how total flow will be determined (Air:  sum of terminal flows via BAS calibrated readings or via hood readings of all terminals, supply (SA) and return air (RA) pitot traverse, SA or RA flow stations.  Water:  pump curves, circuit setter, flow station, ultrasonic, etc.).




i.
The identification and types of measurement instruments to be used and their most recent calibration date.




j.
Specific procedures that will ensure that both air and water side are operating at the lowest possible pressures and provide methods to verify this.




k.
Confirmation that TAB understands the outside air ventilation criteria under all conditions.




l.
Details of whether and how minimum outside air cfm will be verified and set, and for what level (total building, zone, etc.).




m.
Details of how building static and exhaust fan / relief damper capacity will be checked.




n.
Proposed selection points for sound measurements and sound measurement methods.




o.
Details of methods for making any specified coil or other system plant capacity measurements.




p.
Details of any TAB work to be done in phases (by floor, etc.), or of areas to be built out later.




q.
Details regarding specified deferred or seasonal TAB work.




r.
Details of any specified false loading of systems to complete TAB work.




s.
Details of all exhaust fan balancing and capacity verifications, including any required room pressure differentials.




t.
Details of any required interstitial cavity differential pressure measurements and calculations.




u.
Plan for hand-written field technician logs of discrepancies, deficient or uncompleted work by others, contract interpretation requests and lists of completed tests (scope and frequency).




v.
Plan for formal progress reports (scope and frequency).




w.
Plan for formal deficiency reports (scope, frequency and distribution).



4.
A running log of events and issues shall be kept by the TAB field technicians.  Submit hand-written reports of discrepancies, deficient or uncompleted work by others, contract interpretation requests and lists of completed tests to the CA and CM at least twice a week.



5.
Communicate in writing to the controls contractor all setpoint and parameter changes made or problems and discrepancies identified during TAB which affect the control system setup and operation.



6.
Provide a draft TAB report within two weeks of completion.  A copy will be provided to the CA.  The report will contain a full explanation of the methodology, assumptions and the results in a clear format with designations of all uncommon abbreviations and column headings.  The report should follow the latest and most rigorous reporting recommendations by AABC, NEBB or ASHRAE Standard 111.



7.
Provide the CA with any requested data, gathered, but not shown on the draft reports.



8.
Provide a final TAB report for the CA with details, as in the draft.



9.
Conduct functional performance tests and checks on the original TAB as specified for TAB.


F.
The  Mechanical designer shall coordinate with requirements of the CA and the Contractor.
PART 2 - PRODUCTS

2.1
TEST EQUIPMENT


A.
Division 15 shall provide all test equipment necessary to fulfill the testing requirements of this Division.  

PART 3 - EXECUTION

3.1
SUBMITTALS


A.
Division 15 shall provide submittal documentation relative to commissioning as required in this Section Part 1.

3.2
STARTUP


A.
The HVAC mechanical and controls contractors shall follow the start-up and initial checkout procedures listed in the Responsibilities list in this section.  Division 15 has start-up responsibility and is required to complete systems and sub-systems so they are fully functional, meeting the design objectives of the Contract Documents.  The commissioning procedures and functional testing do not relieve or lessen this responsibility or shift that responsibility partially to the commissioning agent or Owner.


B.
Functional testing is intended to begin upon completion of a system.  Functional testing may proceed prior to the completion of systems or sub-systems at the discretion of the CA and CM.  Beginning system testing before full completion, does not relieve the Contractor from  fully completing the system, including all pre-functional checklists as soon as possible.

3.3
TAB


A.
Refer to the TAB responsibilities in Part 1.2 above.

3.4
FUNCTIONAL PERFORMANCE TESTS


A.
See above for a list of systems to be commissioned and to Part 3.6 for a description of the process.
3.6
OPERATION AND MAINTENANCE (O&M) MANUALS


A.
The following O&M manual requirements do not replace O&M manual documentation requirements elsewhere in these specifications.


B.
Division 15 shall compile and prepare documentation for all equipment and systems covered in Division 15 and deliver this documentation to the General Contractor for inclusion in the O&M manuals, according to this section and General Conditions, prior to the training of owner personnel.


C.
The CA shall receive a copy of the O&M manuals for review.


D.
In addition to documentation that may be specified elsewhere, the controls contractor shall compile and organize at minimum the following data on the control system in labeled 3-ring binders with indexed tabs.



1.
Three copies of the controls training manuals in a separate manual from the O&M manuals.



2.
Operation and Maintenance Manuals containing:




a.
Specific instructions on how to perform and apply all functions, features, modes, etc. mentioned in the controls training sections of this specification and other features of this system.  These instructions shall be step-by-step.  Indexes and clear tables of contents shall be included.  The detailed technical manual for programming and customizing control loops and algorithms shall be included.




b.
Full as-built set of control drawings (refer to Submittal section above for details).




c.
Full as-built sequence of operations for each piece of equipment.




d.
Full points list.  In addition to the updated points list required in the original submittals (Part 1 of this section), a listing of all rooms shall be provided with the following information for each room:





1)
Floor





2)
Room number





3)
Room name





4)
Air handler unit ID





5)
Reference drawing number





6)
Air terminal unit tag ID





7)
Heating and/or cooling valve tag ID





8)
Minimum cfm





9)
Maximum cfm




e.
Full print out of all schedules and set points after testing and acceptance of the system.




f.
Full as-built print out of software program.




g.
Electronic copy on disk of the entire program for this facility.




h.
Marking of all system sensors and thermostats on the as-built floor plan and mechanical drawings with their control system designations.




i.
Maintenance instructions, including sensor calibration requirements and methods by sensor type, etc.




j.
Control equipment component submittals, parts lists, etc.




k.
Warranty requirements.




l.
Copies of all checkout tests and calibrations performed by the Contractor (not commissioning tests).



3.
The manual shall be organized and subdivided with permanently labeled tabs for each of the following data in the given order:




a.
Sequences of operation




b.
Control drawings




c.
Points lists




d.
Controller / module data




e.
Thermostats and timers




f.
Sensors and DP switches




g.
Valves and valve actuators




h.
Dampers and damper actuators




i.
Program setups (software program printouts)



4.
Field checkout sheets and trend logs should be provided to the CA for inclusion in the Commissioning Record Book.


E.
The TAB will compile and submit the following with other documentation that may be specified elsewhere in the Specifications.



1.
Final report containing an explanation of the methodology, assumptions, test conditions and the results in a clear format with designations of all uncommon abbreviations and column headings.



2.
The TAB shall mark on the drawings where all traverse and other critical measurements were taken and cross reference the location in the TAB report.


F.
Review of the commissioning related sections of the O&M manuals shall be made by the A/E and by the CA.  

3.7.
TRAINING OF OWNER PERSONNEL


A.
The General Contractor shall be responsible for training coordination and scheduling and ultimately to ensure that training is completed. 

B.
The CA shall be responsible for overseeing and approving the content and adequacy of the training of Owner personnel for commissioned equipment.

C.
The Mechanical Contractor shall have the following training responsibilities:



1.
Provide the CA with a training plan two weeks before the planned training.


2.
Provide designated Owner personnel with comprehensive orientation and training in the understanding of the systems and the operation and maintenance of each piece of HVAC equipment including, but not limited to, pumps, boilers, furnaces, chillers, heat rejection equipment, air conditioning units, air handling units, fans, terminal units, controls and water treatment systems, etc.



3.
Training shall normally start with classroom sessions followed by hands-on training on each piece of equipment, which shall illustrate the various modes of operation, including startup, shutdown, fire/smoke alarm, power failure, etc.



4.
During any demonstration, should the system fail to perform in accordance with the requirements of the O&M manual or sequence of operations, the system will be repaired or adjusted as necessary and the demonstration repeated.



5.
The appropriate trade or manufacturer's representative shall provide the instructions on each major piece of equipment.  This person may be the start-up technician for the piece of equipment, the installing contractor or manufacturer’s representative.  Practical building operating expertise as well as in-depth knowledge of all modes of operation of the specific piece of equipment are required.  More than one party may be required to execute the training.



6.
The controls contractor shall attend sessions other than the controls training, as requested, to discuss the interaction of the controls system as it relates to the equipment being discussed.



7.
The training sessions shall follow the outline in the Table of Contents of the operation and maintenance manual and illustrate whenever possible the use of the O&M manuals for reference.



8.
Training shall include:




a.
Use of the printed installation, operation and maintenance instruction material included in the O&M manuals.




b.
A review of the written O&M instructions emphasizing safe and proper operating requirements, preventative maintenance, special tools needed and spare parts inventory suggestions.  The training shall include start-up, operation in all modes possible, shut-down, seasonal changeover and any emergency procedures.




c.
Discussion of relevant health and safety issues and concerns.




d.
Discussion of warranties and guarantees.




e.
Common troubleshooting problems and solutions.




f.
Explanatory information included in the O&M manuals and the location of all plans and manuals in the facility.




g.
Discussion of any peculiarities of equipment installation or operation.




h.
The format and training agenda in The HVAC Commissioning Process, ASHRAE Guideline 1-1989R, 1996 is recommended.




i.
Classroom sessions shall include the use of overhead projections, slides, video/audio-taped material as might be appropriate.



9.
Hands-on training shall include start-up, operation in all modes possible, including manual, shut-down and any emergency procedures and preventative maintenance for all pieces of equipment.



10.
The mechanical contractor shall fully explain and demonstrate the operation, function and overrides of any local packaged controls, not controlled by the central control system.



11.
Training shall occur after functional testing is complete, unless approved otherwise by the Owner.



12.
The Mechanical Contractor shall provide training on each piece of equipment according to the following schedule.




Hours

System


    8

Chillers and System


    4

Cooling Towers


    2

Piping Systems


    1

Chemical Treatment


    1

Air Compressors and dryers


    4

Air Handler Units


    2

Variable Speed Drives


    2

Air Terminal Units


    4

Smoke Control Systems

    2

Computer Room AC Units


    1

Split System AC or Heat Pumps


    1

Unit Heaters


    1

Restroom Central Exhaust Fans


    2

Service Hot Water Heaters


    1

Domestic Water Booster Pump


D.
The Controls Contractor shall have the following training responsibilities:



1.
Provide the CA with a training plan four weeks before the planned training.


2.
The controls contractor shall provide designated Owner personnel training on the control system in this facility.  The intent is to clearly and completely instruct the Owner on all the capabilities of the control system.



3.
The standard operating manual for the system and any special training manuals will be provided for each trainee, with three extra copies left for the O&M manuals.  In addition, copies of the system technical manual will be demonstrated during training and three copies submitted with the O&M manuals.  Manuals shall include detailed description of the subject matter for each session.  The manuals will cover all control sequences and have a definitions section that fully describes all relevant words used in the manuals and in all software displays.  Manuals will be approved by the CA.  Copies of audiovisuals shall be delivered to the Owner.



4.
The trainings will be tailored to the needs and skill-level of the trainees.



5.
The trainers will be knowledgeable on the system and its use in buildings.  For the on-site sessions, the most qualified trainers shall be used.  The Owner shall approve the instructor prior to scheduling the training.



6.
During any demonstration, should the system fail to perform in accordance with the requirements of the O&M manual or sequence of operations, the system will be repaired or adjusted as necessary and the demonstration repeated.



7.
The controls contractor shall attend sessions other than the controls training, as requested, to discuss the interaction of the controls system as it relates to the equipment being discussed.



8.
There shall be three training sessions:




a.
Training I.  Control System.  The first training shall consist of 8 hours of actual training.  This training may be held on-site or in the supplier’s facility.  If held off-site, the training may occur prior to final completion of the system installation.  Upon completion, each student, using appropriate documentation, should be able to perform elementary operations and describe general hardware architecture and functionality of the system.  




b.
Training II.  Building Systems.  The second session shall be held on-site for a period of 12 hours of actual hands-on training after the completion of system commissioning.   The session shall include instruction on:





1)
Specific hardware configuration of installed systems in this building and specific instruction for operating the installed system, including HVAC systems, lighting controls and any interface with security and communication systems.





2)
Security levels, alarms, system start-up, shut-down, power outage and restart routines, changing setpoints and alarms and other typical changed parameters, overrides, freeze protection, manual operation of equipment, optional control strategies that can be considered, energy savings strategies and set points that if changed will adversely affect energy consumption, energy accounting, procedures for obtaining vendor assistance, etc.





3)
All trending and monitoring features (values, change of state, totalization, etc.),  including setting up, executing, downloading, viewing both tabular and graphically and printing trends.  Trainees will actually set-up trends in the presence of the trainer.





4)
Every screen shall be completely discussed, allowing time for questions.





5)
Use of keypad or plug-in laptop computer at the zone level.





6)
Use of remote access to the system via phone lines or networks.

7)
Setting up and changing an air terminal unit controller.

8)
Graphics generation

9)
Point database entry and modifications

10)
Understanding DDC field panel operating programming (when applicable)




c.
Training III.  The third training will be conducted on-site six months after occupancy and consist of 8 hours of training.  The session will be structured to address specific topics that trainees need to discuss and to answer questions concerning operation of  the system.


E.
The TAB contractor shall have the following training responsibilities:



1.
TAB shall meet for 8 hours with facility staff after completion of TAB and instruct them on the following:




a)
Go over the final TAB report, explaining the layout and meanings of each data type.




b)
Discuss any outstanding deficient items in control, ducting or design that may affect the proper delivery of air or water.




c)
Identify and discuss any terminal units, duct runs, diffusers, coils, fans and pumps that are close to or are not meeting their design capacity.




d)
Discuss any temporary settings and steps to finalize them for any areas that are not finished.




e)
Other salient information that may be useful for facility operations, relative to TAB.

3.8
WRITTEN WORK PRODUCTS

A. Written work products of Contractors will consist of the start-up and initial checkout plan and the filled out start-up, initial checkout and pre-functional checklists.

3.9
AIR HANDLER UNITS (AHU) CHECKLISTS


A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls to activate the equipment as needed.



2.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
AHU and components (fans, coils, valves, ducts, VFD)


PC-_____



2.
Heat recovery coil, humidifier or evaporative cooling sections

PC-_____


C.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements:


The following testing requirements are an addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both3
	Required Seasonal Test1

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unnoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks with which it is associated.
	Manual
	

	In addition to, or as part of (1) above, the following modes or tests are required:

	2.
	Mixed & supply air, & reset temperature control functions.
	Both
	

	3.
	Economizer functions.
	Both
	Cooling

	4.
	SF, RF and exhaust fan interlocks.
	Either
	

	5.
	No CCV flow when there is HCV flow.
	Both
	

	6.
	CCV & HCV modulation & positive shutoff (no leak-thru).
	Manual
	

	7.
	Duct static pressure (SP) control.
	Both
	

	8.
	Return or exhaust fan tracking and building SP.
	Monitoring
	

	9.
	VFD (or inlet vanes) operation on SF and RF: modulation to minimum, control system PID, proportional band of speed vs controlling parameter, constancy of static pressure, verification of program settings, alarms, etc.
	Both
	2

	10.
	Damper interlocks and correct modulation in all modes, including smoke and fire dampers.
	Manual
	

	11.
	Temperature difference across HC & CC per specifications.
	Manual
	

	12.
	Verification of minimum OSA control through varying VAV box positions.
	Either
	2

	13.
	Heating and cooling coils freeze protection.
	Manual
	2

	14.
	Branch duct control damper control.
	Manual
	

	15.
	Night low limit, morning warmup cycle.
	Either
	

	16.
	Heat recovery operation.
	Monitoring
	

	17.
	Verify TAB reported SF cfm with control system reading.
	Manual
	2

	18.
	All alarms (low limits, high static, etc.).
	Manual
	

	19.
	Heating and cooling coil capacity test, optional.
	Manual
	Design

	20.
	Sensor and actuator calibration checks:  on duct static pressure sensor on SAT, MAT, OSAT, OSA & RA damper and valve positions, SF cfm reading with TAB, and other random checks (EMS readout against hand-held calibrated instrument or observation must be within specified tolerances)
	Manual
	

	21.
	Verify schedules and setpoints to be reasonable and appropriate
	
	


1Cooling season, Heating season or Both.  “Design” means within 5(of season design (ASHRAE 2 1/2%), or 95% of loading design.  A blank cell denotes no special seasonal test is required and that test can be executed during any season, if condition simulation is appropriate.

2Seasonal test not required if seasonal conditions can be adequately simulated.

3Refer to Special Procedures


E.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



1.
Reduced Testing for Smaller Units.  For standard application AHU’s less than 15 tons, the following modifications to the testing requirements apply:  1) either Manual or Monitoring will satisfy the verification requirement--where Both is listed, choose one.  2) Testing Modes 6, 8, 11, 13 and 16  is not required.


F.
Required Monitoring  



1.
All points listed below  which are control system monitored points shall be trended by the controls contractor.  Other points shall be monitored by the CA using dataloggers.  

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	For each AHU being tested:
	
	
	
	

	RAT
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	SAT
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	CC LAT (optional)
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	HC LAT (optional)
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	MAT
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	Indoor WB or enthalpy, if enthalpy economizer
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	SF speed, if variable, else status
	5
	5 days incl. weekend
	Y
	Y
	1, 5-9

	RF speed, if variable, else status
	5
	5 days incl. weekend
	Y
	Y
	1, 5-9

	Duct SP
	5
	5 days incl. weekend
	Y
	Y
	1, 7, 9

	Building SP differential
	5
	5 days incl. weekend
	Y
	Y
	8

	OSAT
	5
	5 days incl. weekend
	Y
	Y
	All

	OSA-WB or enthalpy, if enthalpy economizer
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	Indoor dry-bulb ___zones (expected to be most problematic)
	5
	5 days incl. weekend
	Y
	Y
	All

	
	
	
	
	
	




Remarks:




CCV position (optional)




HCV position (optional)




SF cfm not required if not monitored




RF cfm not required if not monitored


G.
Acceptance Criteria  (referenced by function or mode ID)



1-21.
For the conditions, sequences and modes tested, the AHU, integral components and related equipment respond to varying loads and changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.



2.

AHU with supporting systems shall be able to maintain the SA temperature within 1.0F either side of the deadband of the current setpoint without excessive hunting.



7.

AHU and controls shall control the duct static pressure so that it does not drift more than an amount equal to 10% of the setpoint value either side of the deadband without excessive hunting.


H.
Sampling Strategy for Identical Units



1.
All identical AHU’s over 15 tons shall not have any sampling--test all units.  However, 25% of the units may have monitoring be the verification method for modes listed with Monitoring or Both as testing methods, with no less than three units being fully tested per the above requirements.



2.
All identical AHU’s equal to or less than 15 tons shall be sampled:




Randomly test at least 50%  of each group of identical equipment (the 1st sample) per the above tests.  In no case test less than three units in each group. If 20%  of the units in the first sample fail the functional performance tests, test another the remaining 50%, fully at the contractor’s expense.  This sampling applies to the testing subsections.  That is, if calibration is off on more than 10% of the tested piece of equipment, then another sample shall have calibrations checked, but not all other tests need to be done on the second sample.



3.
All units not included in the sampling testing and monitoring shall be fully monitored for the monitoring modes listed above in the monitoring section.

3.10.
BUILDING AUTOMATION SYSTEM  (BAS) CHECKLISTS

A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls to activate the equipment.



2.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Building Automation System




PC-_____



2.
All pre-functional checklists of controlled equipment

    ---


D.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


E.
A significant part of the BAS functional testing requirements is the successful completion of the functional tests of equipment the BAS controls or interlocks with.  Uncompleted equipment functional tests or outstanding deficiencies in those tests lend the required BAS functional testing incomplete.  


F.
Integral or stand-alone controls are functionally tested with the equipment they are attached to, including any interlocks with other equipment or systems and thus are not covered under the BAS testing requirements, except for any integrated functions or interlocks listed below.


G.
In addition to the controlled equipment testing, the following tests are required for the BAS, where features have been specified. The following testing requirements are in addition to and do not replace any testing requirements elsewhere in the specifications.

	
	

Function / Mode
	Test Method
Manual (demonstration), Monitoring, Either or Both

	MISC. FUNCTIONS

	1.
	All specified functions and features are set up, debugged and fully operable
	Verbal discussion of features

	2.
	Power failure and battery backup and power-up restart functions
	Demonstration

	3.
	Specified trending and graphing features demonstration
	See equipment trends

	4.
	Global commands features
	Demonstration

	5.
	Security and access codes
	Demonstration

	6.
	Occupant over-rides (manual, telephone, key, keypad, etc.)
	Demonstration

	7.
	O&M schedules and alarms
	Demonstration

	8.
	Scheduling features fully functional and setup, including holidays
	Observation in terminal screens or printouts

	9.
	Date and time setting in central computer and verify field panels read the same time
	Demonstration

	10.
	Included features not specified to be setup are installed (list)
	Demonstration

	11.
	Occupancy sensors and controls
	Demonstration

	12.
	Demonstrate functionality of field panels using local operator keypads and local ports (plug-ins) using portable computer/keypad
	Demonstration of 100% of panels and 10% of ports

	13.
	All graphic screens and value readouts completed
	Demonstration

	14.
	Setpoint changing features and functions
	Done during equipment testing

	15.
	Communications to remote sites
	Demonstration

	16.
	Sensor calibrations
	Sampled during equipment tests

	17.
	“After hours” use tracking and billing
	

	18.
	Final as-builts or redlines (per spec) control drawings, final points list, program code, setpoints, schedules, warranties, etc. per specs, submitted for O&Ms.
	Observation

	19.
	Verify that points that are monitored only, having no control function, are checked for proper reporting to BAS.
	Observation

	INTEGRATED TESTS

	20.
	Fire alarm interlocks and response
	Demonstration

	21.
	Duty cycling (if specified)
	Monitoring

	22.
	Demand limiting (including over-ride of limiting)
	Monitoring

	23.
	Sequential staging ON of equipment
	Either

	24.
	Optimum start-stop functions
	Monitoring

	25.
	All control strategies and sequences not tested during controlled equipment testing
	Either

	26.
	Other integrated tests specified in the contract documents
	

	27.
	Security system interlocks
	Demonstration

	28.
	Fire protection and suppression systems
	Demonstration



H.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



None


I.
Additional Required Monitoring  



1.
Besides the trending and monitoring required with the functional testing of equipemint, all points listed below which are control system monitored points shall be trended by the controls contractor.  Other points shall be monitored by the CA using dataloggers.  

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	Misc. equipment current or status for duty cycling and demand limiting
	5
	5 days incl. weekend
	Y
	Y
	21-22

	Equipment or building kW or current for demand limiting
	5
	5 days incl. weekend
	Y
	Y
	21-22

	Optimum start/stop equip.
	5
	5 days incl. weekend
	Y
	Y
	24




Remarks:


I.
Acceptance Criteria  (referenced by function or mode ID)



All
For the conditions, sequences and modes tested, the BAS, integral components and related equipment respond to changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.


J.
Sampling Strategy for Identical Units



1.
Sample 10% of the field panels for procedure 9, and 10% of the local ports for procedure 12. If 10%  fail, test another 10%. If 10% of those fail, test all remaining units at the contractor’s expense.

3.11
CHILLER CHECKLISTS

(Note)The cooling tower can be tested integrally with the chiller testing.  The cooling tower test 
requirements shall be as listed elsewhere.


A.
Parties Responsible to Execute Functional Test



1.
Controls contractor shall operate the controls as needed.



2.
HVAC mechanical contractor or vendor shall assist in testing sequences as needed.



3.
CA shall witness, direct and document testing.


B.
The applicable prerequisite checklist shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent shall also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


C.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Chiller








PC-_____



2.
Primary CHW supply pumps





PC-_____



3.
Chilled water piping system





PC-_____



4.
Secondary CHW supply pumps





PC-_____



5.
VFD on secondary pumps





PC-_____



6.
Cooling tower







PC-_____


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements



The following testing requirements are an addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both
	Required Seasonal Test1

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unnoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks with which it is associated. A full cycle from no load to full load and then to no load and compressors off shall be demonstrated.
	Manual
	

	In addition to, or as part of (1) above, the following modes or tests are required:

	2.
	Primary Side.  Lead/lag staging of chillers, optimization, capacity modulation (loading and unloading), heat reclaim, and primary CHW supply pumps, all relating to maintaining CDW and CHW temperatures.
	Both
	Cooling

	3.
	Secondary Side.  Secondary CWH supply pump staging, bypass valve operation, if no VFD and CHWT reset.  VFD operation: modulation to minimum, control system PID, proportional band of speed vs controlling parameter, alarms, verification of program settings, etc.
	Both
	Cooling

	4.
	All alarms:  high and low pressure, low oil, etc.
	Manual
	

	5.
	Test each possible lead chiller as lead chiller, and each pump as lead pump, including standby pumps.
	Manual
	

	6.
	kW/ton and APLV efficiency test, optional
	Manual
	Cooling

	7.
	Capacity test, optional
	Manual
	Cooling Design

	8.
	Sensor and actuator calibration checks on: ECDWT, CHWST, pressure sensor controlling pump speed, 3-way valve, and other random checks (EMS readout against handheld calibrated instrument must be within 0.5(F for temps. or within a tolerance equal to 10% of the pressure setpoint, with a test gage)
	Manual
	

	9.
	Verify schedules and setpoints to be reasonable and appropriate
	
	


1Cooling season, Heating season or Both.  “Design” means within 5(F of season design (ASHRAE 2 1/2%), or 95% of loading design.  A blank cell denotes no special seasonal test is required and that test can be executed during any season, if condition simulation is appropriate.


E.
Special Procedures  (other equipment with which to test, etc.; reference to function ID)



1.
Test with cooling tower in automatic mode.



2.
False load chiller, if necessary.


F.
Required Monitoring  



1.
All points listed below which are control system monitored points shall be trended by the controls contractor.  Other points shall be monitored by the CA using dataloggers.  

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	For each chiller and pump:
	
	
	
	

	Chiller current
	5
	5 days incl. weekend
	Y
	Y
	1-3

	ECDWT
	5
	5 days incl. weekend
	Y
	Y
	1-3

	LCDWT
	5
	5 days incl. weekend
	Y
	Y
	1-3

	CDW pump current or status
	5
	5 days incl. weekend
	Y
	Y
	1-3

	CHWST
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	CHWRT
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	OSAT-DB
	5
	5 days incl. weekend
	Y
	Y
	1-3

	CHWS primary pump current or status
	5
	5 days incl. weekend
	Y
	Y
	1, 2

	CHWS secondary pump speed, if variable
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	CHWS secondary pump flow rate
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	CHWS secondary pump speed controlling parameter value
	5
	5 days incl. weekend
	Y
	Y
	1, 3




Remarks:


G.
Acceptance Criteria  (referenced by function or mode ID)



1-9.
For the conditions, sequences and modes tested, the chillers, integral components and related equipment respond to varying loads and changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.



2.
Chiller shall maintain the chilled water supply setpoint to within +/- 1.0F of setpoint deadband without excessive hunting.



9.
Pumping system and controls shall maintain the current desired pressure setpoint to within an amount equal to 10% of the setpoint value either side of the deadband without excessive hunting.


H.
Sampling Strategy for Identical Units



1.
No sampling, test all.

3.12
COOLING TOWER CHECKLISTS


(Note)The cooling tower can be tested integrally with the chiller testing.


A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls, as needed.



2.
HVAC mechanical contractor or vendor:  assist in testing sequences, as needed.



3.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Condenser water pump






PC-____



2.
Cooling tower and components





PC-____



3.
Condenser water piping system





PC-____



4.
Fan VFD








PC-____


C.
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements:


The following testing requirements are an addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both
	Required Seasonal Test1

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unnoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks with which it is associated.
	Manual
	

	In addition to, or as part of (1) above, the following modes or tests are required:

	2.
	Cooling season modes of operation.
	Both
	Cooling

	3.
	Heating season modes of operation.
	Both
	Heating

	4.
	Lead/lag staging of towers, including testing each tower as lead tower.  Staging of fans, spray pumps, condenser pumps, CDWT reset, time delays.
	Both, except2
	

	5.
	Bypass valve operation and ability of CT to maintain entering CDW temperature.
	Either
	

	6.
	Sump heater and freeze protection operation.
	Either
	Heating

	7.
	All alarms:  vibration, fan failure, high water, low water.
	Manual
	

	8.
	Verify approach temperature with manuf. specs, optional.
	Either
	

	9.
	VFD operation: modulation to low limit, controlling PID, proportional band of speed vs control parameter, verification of program settings, alarms.
	Both
	

	10.
	Capacity test, optional.
	Manual
	Clg. Des.

	11.
	Sensor and actuator calibration checks:  See Chiller requirements.
	Manual
	

	12.
	Verify schedules and setpoints to be reasonable and appropriate.
	
	


1Cooling season, Heating season or Both.  “Design” means within 5(F of season design (ASHRAE 2 1/2%), or 95% of loading design.  A blank cell denotes no special seasonal test is required and that testing can be executed during any season, if condition simulation is appropriate.

2Monitoring testing each tower as lead tower is not necessary.


E.
Special Procedures or Conditions  (other equipment to test with, etc.; reference to function ID)



1.
Tests to be made with chiller in automatic mode.



2.
False load chiller, if necessary.


F.
Required Monitoring  



1.
All points listed below which are control system monitored points shall be trended by the controls contractor.  Other points shall be monitored by the CA using dataloggers.  

	Point
	Time Step
(min.)
	Minimum
Time Period 
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	For each CT:

	CDEWT
	5
	Wed. - Sat
	Y
	Y
	1, 2, 4, 9

	CDLWT
	5
	Wed. - Sat
	Y
	Y
	1, 2, 4, 8, 9

	OSAT-DB
	5
	Wed. - Sat
	Y
	Y
	1, 2, 4, 8,9

	OSAT-WB (optional)
	5
	Wed. - Sat
	Y
	Y
	8

	Fan motor speed, stage or current
	5
	Wed. - Sat
	Y
	Y
	4, 9

	CDW pump status or current
	5
	Wed. - Sat
	Y
	Y
	1, 2, 4, 9

	Each chiller status or current
	5
	Wed. - Sat
	Y
	Y
	1, 2, 4, 9

	
	
	
	
	
	




Remarks:


G.
Acceptance Criteria  (referenced by function or mode ID)



1-12.
For the conditions, sequences and modes tested, the cooling tower(s), integral components and related equipment respond to varying loads and changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.



5.

Cooling tower should be able to maintain the current specified setpoint for entering condenser water to within +/- 2F, when outside conditions do not restrict this thermodynamically.


H.
Sampling Strategy for Identical Units



1.
No sampling, test all.

3.13
EXHAUST FANS CHECKLISTS


(NOTE)The testing requirements apply to the following fans (check all that apply): __central restroom,   __mechanical room, __stairwell pressurization,  __elevator pressurization, __kitchen hood, __garage

A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls to activate the equipment, if BAS controlled.



2.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Exhaust fans







PC-_____


C.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements



The following testing requirements are in addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both1
	Required Seasonal Test

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unnoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks that it is associated with.
	Manual
	

	In addition to, or as part of (1) above, the following modes or tests are required:

	2.
	Verify schedules and setpoints to be reasonable and appropriate
	
	

	3.
	Function at fire alarm (off, depressurization, etc.)
	Manual
	

	4.
	Interlocks to building pressurization control
	Manual
	

	5.
	Speed controls
	Either
	

	6.
	Check TAB report record of sound power level tests and space pressures and compare to specifications
	Review
	

	7.
	Sensor calibration checks on any controlling temperature or pressure sensor
	Manual
	




1Refer to Special Procedures


E.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



None


F.
Required Monitoring  



1.
All points listed below which are control system monitored points shall be trended by the controls contractor.  Other points shall be monitored by the CA using dataloggers.  

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	For each fan:
	
	
	
	

	Do be determined
	
	
	
	
	

	
	
	
	
	
	




Remarks:


G.
Acceptance Criteria  (referenced by function or mode ID)



1-6.
For the conditions, sequences and modes tested, the fans, integral components and related equipment respond to changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.


H.
Sampling Strategy for Identical  Units of the same type and function, but different in size, are considered identical for sampling purposes.



1.
Randomly test at least 10%  of each group of identical equipment (the 1st sample).  In no case test less than three units in each group. If 10%  of the units in the first sample fail the functional performance tests, test another 10% of the group (the 2nd sample). If 10% of the units in the 2nd sample fail, test all remaining units in the whole group, fully at the contractor’s expense.  This sampling applies to the testing subsections.  That is, if calibration is off on more than 10% of the tested piece of equipment, then another sample shall have calibrations checked, but not all other tests need to be done on the second sample.

3.14
INDOOR AIR CLIMATE CONTROL--MISC. SYSTEMS CHECKLISTS

(NOTE)At least 10% of all space zones shall be verified to be maintaining proper climate control. Specific test requirements for this may have been identified elsewhere in this specification (e.g., under terminal units).  For all areas not specifically specified, otherwise, the following tests shall be conducted.


A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls and provide trend logs



2.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested





1.
Cooling plant (entire system)









2.
Heating plant (entire system)





3.
Air, water or steam distribution system



4.
Control system







C.
Prerequisites
All listed systems in Part B, above, shall have had successful functional tests completed prior to this test.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements



This is a performance test to verify that the HVAC systems can provide and maintain the temperature and relative humidity levels specified, during normal and extreme weather and occupancy conditions. The test consists of monitoring, via trend logs, of various points during the cooling season when temperatures reach to within 5(F of season design (ASHRAE 2 1/2%).


E.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



1.
Building should be normally occupied during the test.


F.
Required Monitoring  



1.
All points listed below  which are control system monitored points shall be trended by the controls contractor. 

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	Space temperature control:
	
	
	
	

	Space temperature
	5
	5 days incl. weekend
	Y
	Y
	1-3

	OSAT-DB
	5
	5 days incl. weekend
	Y
	Y
	1-3




Remarks:


G.
Acceptance Criteria  (referenced by function or mode ID)



1.
Space temperature during occupied modes shall average within +/- 1(F of setpoint and always remain within 1(F of the ends of the deadband without excessive hunting of either the applicable damper or coil valve, or complaints of drafts or stuffiness from occupants.


H.
Sampling Strategy for Identical  Units of the same type and function, but different in size, are considered identical for sampling purposes.



1.
Randomly test at least 10%  of each group of identical equipment (the 1st sample).  In no case test less than three units in each group. If 10%  of the units in the first sample fail the functional performance tests, test another 10% of the group (the 2nd sample). If 10% of the units in the 2nd sample fail, test all remaining units in the whole group, fully at the contractor’s expense.  This sampling applies to the testing subsections.  That is, if calibration is off on more than 10% of the tested piece of equipment, then another sample shall have calibrations checked, but not all other tests need to be done on the second sample.

3.15
INDOOR AIR QUALITY CHECK (IAQ) CHECKLISTS
(Note)IAQ checking activities are not technically “functional testing.”  However, they are included here for consistency.  Indoor air quality (IAQ) commissioning does not ensure that indoor air quality will be adequate or without deficiency at building turnover or during occupancy, unless the owner has specifically specified that actual air quality testing be performed.  Commissioning for indoor air quality entails performing tasks that minimize the potential for IAQ problems, but it does not eliminate their possibility.  .


A.
Parties Responsible to Perform IAQ Checks



1.
CA:  performs and oversees checks, inspections and reviews.



2.
TAB contractor:  performs checks using test instruments for tasks under Part C


B.
Prerequisites
CA will perform each check and review as soon as the materials or work is such that IAQ related determinations can be made.


C.
Purpose.  The purpose of the IAQ check is to minimize the potential for IAQ problems in the facility during occupancy.  The CA is not responsible for any IAQ issues during construction, nor for IAQ issues in the occupied part of the facility, if construction is being performed in other parts of the facility.


D.
The following tasks will be conducted and documented:

1.  Submittal Reviews Compare specified data with submitted data sheets for the following:

a. Filtration and filter type.

b. Materials that had specifications for emissions rates as part of the contract documents.

c. HVAC materials that have a potential for airflow erosion, corrosion and microbial contamination (HVAC insulation materials, etc.).

d. Manufacturer’s safety data sheets (MSDS) for products specified in the contract documents that may be suspected contributors to indoor pollutants  (carpets, flooring, fabrics, adhesives, wall coverings, partitions, and ceilings; insulating and fire‑proofing materials; sealants on walls and floors; use of preservatives, paints, varnishes, and other finish materials).

2.  Static Inspections and Checks

a. Review the code compliance calculations for accuracy.

b. Verify that the outdoor air intakes are sized and located according the plans and specifications.

c. Verify that no outside conditions exist that could compromise the quality of the air entering the outdoor intakes.

d. Inspect air intakes and exhausts for short‑circuiting.

e. Document any required ductwork cleaning.

f. Prior to building turnover, verify that final filters are installed and coils, inside of units and ductwork is clean.

g. Inspect air supply system components to ensure control and minimization of the presence of free and standing water and to minimize microbial contamination (condensate trays, traps, humidifiers, water baffles, mist eliminators and cooling towers).

h. Verify proper access for cleaning of both sides of coils, condensate pans and/or humidifier reservoirs in all HVAC equipment.

i. Meet with contractors and review any specified manufacturer’s recommended curing, drying and airing procedures (for minimizing emission rates).  Document the compliance of the contractors.

j. When the building is partially occupied during construction, meet with the Contractor and issue a plan in writing for operation of the HVAC system.  The plan will describe how the system can be operated at as close to normal operating conditions as possible, to minimize dust and dirt from contaminating the ductwork and coils and polluting the occupied areas, and to prevent damaging moisture migration.

k. Review TAB reports for consistency with the specifications.

l. After completion of TAB, review with the TAB contractor, any areas they may consider as being potentially problematic regarding maintaining adequate minimum outdoor air, proper exhaust or room pressure differential.

3.  Air Flow and Pressurization Checks

a. Verify that the specified minimum ventilation rates are maintained during all occupied modes of operation, particularly during VAV terminal box turn-down.

b. Spot-check TAB supply air flow readings in critical areas.

c. Spot-check the TAB measurements and setup of the exhaust systems for each area.  When purging is specified in the contract documents, develop a plan for, and see that the Contractor purges the building prior to occupancy.

d. Verify that the total building pressurization criteria is met through varying HVAC loads and economizing conditions.

e. Verify that room pressure differentials are as specified between critical areas (clean rooms, bio-hazards, film developing rooms, chemical storage areas, etc.).

f. Verify that the design engineer’s specification for interstitial and area pressurization differentials has been met.


4.  Verification

a. Verify that the specified ventilation effectiveness throughout the various areas of the building is being met by:   ___smoke tube testing for airflow patterns,  ___flow hood readings,   ___air contaminant monitoring,   ___other_________________________________________________.

b. Perform IAQ testing using the following methods (surface cultures for microbial contamination, airborne culture testing, CO2 monitoring, VOC monitoring, CO monitoring, etc.).


E.
Acceptance Criteria 
Unless noted in the requirements, the commissioning agent in concert with the CM will make determinations and interpretations for when IAQ issues are considered to be in compliance with the contract documents.

3.16
PACKAGED DX AIR CONDITIONING CHECKLISTS

A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls to activate the equipment.



2.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Unit (fans, coils, condenser, compressors, ducts, VFD)


PC-_____



2.
Heat recovery coil
, humidifier or direct / indirect

evaporative cooling sections





PC-_____


C.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements



The following testing requirements are in addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both3
	Required Seasonal Test1

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unnoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks that it is associated with.
	Manual
	

	In addition to, or as part of (1) above, the following modes or tests are required:

	2.
	Mixed and supply air, and reset temp. control functions
	Both
	

	3.
	Economizer functions
	Both
	Cooling

	4.
	SF, RF and exhaust fan interlocks
	Either
	

	5.
	Compressor unloading & condenser fan staging for head pressure control
	Both
	

	6.
	Demand limiting control (if applicable)
	Monitoring
	Cooling

	7.
	Duct static pressure (SP) control
	Both
	

	8.
	Return or exhaust fan tracking and building SP
	Monitoring
	

	9.
	VFD (or inlet vanes) operation on SF and RF: modulation to minimum, control system PID, proportional band of speed vs controlling parameter, constancy of static pressure, verification of program settings, alarms, etc
	Both
	2

	10.
	Damper interlocks and correct modulation in all modes, including fire and smoke dampers
	Manual
	

	11.
	Temperature difference across heating and cooling coils, if spec’d
	Manual
	

	12.
	Verification of minimum OSA quantity and control through varying VAV box positions
	Either
	2

	13.
	Branch duct control damper control
	Manual
	

	14.
	Night low and high limit, morning warmup cycle, 
	Either
	

	15.
	Heat recovery operation
	Monitoring
	

	16.
	Verify TAB reported SF cfm with control system reading
	Manual
	2

	17.
	All alarms (low limits, high static, freezestat, etc.)
	Manual
	

	18.
	Unit heating and cooling capacity tests, optional
	Manual
	Design

	19.
	Heating and cooling EER or COP efficiency tests, optional
	
	Design

	20.
	Change over function from heating to cooling and defrost (heatpumps)
	Manual
	

	21.
	Sensor and actuator calibration checks on:  duct static pressure sensor on units >10 tons, SAT, MAT, OSAT, economizer and RA dampers and other random checks (EMS readout against hand-held calibrated instrument must be within 0.5(F for temps. or within a tolerance equal to 10% of static pressure setpoint, with an inclined manometer)
	Manual
	

	22.
	Verify control strategies, schedules and setpoints to be reasonable and appropriate
	
	


1Cooling season, Heating season or Both.  “Design” means within 5(of season design (ASHRAE 2 1/2%), or 95% of loading design.  A blank cell denotes no special seasonal test is required and that test can be executed during any season, if condition simulation is appropriate.

2Seasonal test not required if seasonal conditions can be adequately simulated.

3Refer to Special Procedures


E.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



1.
Reduced Testing for Smaller Units.  For standard application AHU’s less than 15 tons, the following modifications to the testing requirements apply:  1) either Manual or Monitoring will satisfy the verification requirement--where Both is listed, choose one.  2) Testing Modes 6, 8, 11, 13 and 16  is not required.


F.
Required Monitoring  



1.
All points listed below  which are control system monitored points shall be trended by the controls contractor.  Other points shall be monitored by the CA using dataloggers.

`

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	For each Unit being tested:
	
	
	
	

	RAT
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5, 19

	SAT
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	CC LAT
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	HC LAT
	5
	5 days incl. weekend
	Y
	Y
	1-3, 5

	MAT
	5
	5 days incl. weekend
	Y
	Y
	1, 3, 19

	Indoor WB or enthalpy
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	SF speed
	5
	5 days incl. weekend
	Y
	Y
	1, 5-9

	RF speed
	5
	5 days incl. weekend
	Y
	Y
	1, 5-9

	Duct SP
	5
	5 days incl. weekend
	Y
	Y
	1, 7, 9

	Building SP differential
	5
	5 days incl. weekend
	Y
	Y
	8

	OSAT
	5
	5 days incl. weekend
	Y
	Y
	All

	OSAT-WB or enthalpy
	5
	5 days incl. weekend
	Y
	Y
	1, 3

	Indoor dry-bulb ___zones
	5
	5 days incl. weekend
	Y
	Y
	All

	Compressor amps or stage
	5
	5 days incl. weekend
	Y
	Y
	5

	Condenser fan amps or stage
	5
	5 days incl. weekend
	Y
	Y
	5




Remarks:


G.
Acceptance Criteria  (referenced by function or mode ID)



1-22.  
For the conditions, sequences and modes tested, the system, integral components and related equipment respond to varying loads and changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.



2.

RTU shall be able to maintain the SA temperature within 1.0F either side of the deadband of the current setpoint without excessive hunting.



7.

RTU and controls shall control the duct static pressure so that it does not drift more than an amount equal to 10% of the setpoint value either side of the deadband without excessive hunting.


H.
Sampling Strategy for Identical Units



1.
All identical AHU’s over 15 tons shall not have any sampling--test all units.  However, 25% of the units may have monitoring be the verification method for modes listed with Monitoring or Both as testing methods, with no less than three units being fully tested per the above requirements.



2.
All identical AHU’s equal to or less than 15 tons shall be sampled:




Randomly test at least 50%  of each group of identical equipment (the 1st sample) per the above tests.  In no case test less than three units in each group. If 20%  of the units in the first sample fail the functional performance tests, test another the remaining 50%, fully at the contractor’s expense.  This sampling applies to the testing subsections.  That is, if calibration is off on more than 10% of the tested piece of equipment, then another sample shall have calibrations checked, but not all other tests need to be done on the second sample.



3.
All units not included in the sampling testing and monitoring shall be fully monitored for the monitoring modes listed above in the monitoring section.

3.17
SERVICE HOT WATER SYSTEM CHECKLISTS

A.
Parties Responsible to Execute Functional Test



1.
CA: perform and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Hot water heaters (heaters, mixing valves)



PC-_____



2.
Recirculating pumps






PC-_____


C.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements



The following testing requirements are in addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both
	Required Seasonal Test

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unnoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks that it is associated with.
	Manual
	

	In addition to, or as part of (1) above, the following modes or tests are required:

	2.
	Verify schedules and setpoints to be reasonable and appropriate
	
	

	3.
	Unoccupied pump operation
	Either
	

	4.
	Mixing valve operation and temperature control
	Either
	

	5.
	Sensor calibration checks on hot water temperature
	Manual
	

	
	
	
	



E.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



None


F.
Required Monitoring



None


G.
Acceptance Criteria  (referenced by function or mode ID)



1-6.
For the conditions, sequences and modes tested, the fan’s integral components and related equipment respond to changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.


H.
Sampling Strategy for Identical Units



1.
No sampling.  Test all units.

3.18
TERMINAL UNITS CHECKLISTS
(This applies to standard applications, critical applications will have additional tests and a higher fraction tested.)


A.
Parties Responsible to Execute Functional Test



1.
Controls contractor:  operate the controls to activate the equipment.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
Terminal unit (TU)






PC-_____


C.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Functions / Modes Required To Be Tested, Test Methods and Seasonal Test Requirements



The following testing requirements are in addition to and do not replace any testing requirements elsewhere in this Division.

	
	Function / Mode
	Test Method
Manual, Monitoring, Either or Both3
	Required Seasonal Test1

	General
	
	

	1.
	Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, warmup, shutdown, unnoccupied & manual modes and power failure and restoration. Test functionality of this piece of equipment or system in all control strategies or interlocks that it is associated with, including all damper, valve and fan functions.
	Manual
	

	In addition to, or as part of  (1) above, the following modes or tests are required:

	2.
	Sensor activator calibration checks on: SAT, MAT, zone air temperature damper position and other random checks (EMS readout against visual or hand-held calibrated instrument must be within 0.5(F for temps. or within a tolerance equal to 10% of static pressure setpoint, with an inclined manometer)
	Manual
	

	3.
	Device and actuator calibration and stroke checks for heating coil valve and non-DDC dampers
	Manual
	

	4.
	For the TU’s tested, check the prefunctional checklist items.
	Observation
	

	5.
	Verify control parameters and setpoints to be reasonable and appropriate by reviewing the full program of 5% of all the TU’s with each other for consistency.  Verify the max. and min. cfm setpoints of all tested TU’s against the control drawing and TAB values.  Verify other  TU programming parameters such as K-factors, deadbands, setpoints, stroke times, etc.
	Observation
	

	6.
	Verify no CCV flow when there is HCV flow
	Either
	

	7.
	Verify no hunting or significant overshoot by damper or valves.
	Either
	

	8.
	Verify by measurement, CCV & HCV positive shutoff (no leak-thru)
	Manual
	

	9.
	Verification of minimum OSA control through varying VAV box positions, if applicable
	Either
	2

	10.
	All alarms (fan status, low limits, high static, etc.)
	Manual
	

	11.
	Verify that TU is maintaining space setpoint temperatures
	Monitoring
	Both
Design

	12.
	Verify airflows and pressures (this random test is part of the TAB test)
	--
	


NOTES:

1Cooling season, Heating season or Both.  “Design” means within 5(F of season design (ASHRAE 2 1/2%), or 95% of loading design.  A blank cell denotes no special seasonal test is required and that test can be executed during any season, if condition simulation is appropriate.

2Seasonal test not required if seasonal conditions can be adequately simulated.

3Refer to Special Procedures


E.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



None


F.
Required Monitoring  



1.
All points listed below  which are control system monitored points shall be trended by the controls contractor. Other points shall be monitored by the CA using dataloggers. 

	Point
	Time Step
(min.)
	Minimum
Time Period
of Trend
	Hard Copy?
(Y/N)
	ASCII File? (Y/N)
	
Function 
Being Tested

	For each zone thermostat and space sensor and other critical areas, monitor:


	Space temperature
	10
	3 weekdays, 
summer design
	Y
	Y
	11


	Space temperature
	10
	3 weekdays, 
winter design
	Y
	Y
	11

	Space temperature
	2
	8 hours, occupied
	Y
	Y
	7

	Heating coil valve
	2
	8 hours, occupied
	Y
	Y
	7

	Damper position or cfm
	2
	8 hours, occupied
	Y
	Y
	7




Remarks:


G.
Acceptance Criteria  (referenced by function or mode ID)



1-11.
For the conditions, sequences and modes tested, the TU, integral components and related equipment respond to varying loads and changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.



10.

Space temperature during occupied modes shall average within +/- 1(F of setpoint and always remain within 1(F of the ends of the deadband without excessive hunting of either the damper or coil valve, or complaints of drafts or stuffiness from occupants.


H.
Sampling Strategy for Identical  Units of the same type and function, but different in size, are considered identical for sampling purposes.



1.
Testing.  Randomly test at least 10%  of each group of identical equipment (the 1st sample).  In no case test less than three units in each group. If 10%  of the units in the first sample fail the functional performance tests, test another 10% of the group (the 2nd sample). If 10% of the units in the 2nd sample fail, test all remaining units in the whole group, fully at the contractor’s expense.  This sampling applies to the testing subsections.  That is, if calibration is off on more than 10% of the tested piece of equipment, then another sample shall have calibrations checked, but not all other tests need to be done on the second sample.



2.
Monitoring.  Ten percent of the total number of zones in the building, chosen by the Owner, shall be monitored. Within this 10%, shall be included a distribution of all air handlers, zones expected to have the greatest heating and cooling demand, perimeter and core zones and zones identified from the commissioning process that have exhibited potential problems.

3.19
TEST AND BALANCE WORK  (TAB) CHECKLISTS

A.
Parties Responsible to Execute Functional Test



1.
TAB contractor:  perform checks using test instruments.



2.
Controls contractor:  operate the controls to activate the equipment.



3.
CA: to witness, direct and document testing.


B.
Integral Components or Related Equipment Being Tested

Pre-functional Checklist ID



1.
TAB water-side







PC-_____



2.
TAB air-side







PC-_____


C.
Prerequisites
The applicable prerequisite checklist items shall be listed on each functional test form and checked off prior to functional testing. The commissioning agent will also spot-check misc. items and calibrations on the pre-functional checklists previously completed by the installer, before the beginning of functional testing.


D.
Purpose.  The purpose of this test is to spot check the TAB work to verify that it was done in accordance with the contract documents and acceptable practice and that the TAB report is accurate.


E.
The following tests and checks will be conducted. The following testing requirements are in addition to and do not replace any testing requirements elsewhere in this Division.

	
	Test or Check
	Test Method
	Required Seasonal Test3

	1.
	A random sample of up to _____ % the TAB report data shall be selected for verification (air velocity, air or water flow rate, pressure differential, electrical or sound measurement, etc.).  The original TAB contractor will execute the checks, witnessed by the commissioning authority.  The TAB contractor will use the same test instruments as used in the original TAB work.

A failure1 of more than 10% of the selected items of a given system2 shall result in the failure of acceptance of the system TAB report and the TAB contractor shall be responsible to rebalance the system, provide a new system TAB report and repeat random verifications of the new TAB report.

The random testing will include the verification of minimum outdoor air intake flows at minimum, maximum and intermediate total airflow rates for _____% of the air handlers.  Other selected data to be verified will be made known upon day of testing.


	Demonstration
	

	2.
	Verify that final settings of all valves, splitters, dampers and other adjustment devices have been permanently marked by the TAB Contractor.
	Demonstration
	

	3.
	Verification that the air system is being controlled to the lowest possible static pressure while still meeting design loads, less diversity.  This shall include a review of TAB methods, control setpoints established by TAB and a physical verification of at least one leg from fan to diffuser having all balancing dampers wide open and that during full cooling of all TUs taking off downstream of the static pressure sensor, the TU on the critical leg has its damper 90% or more open.
	Demonstration
	

	4.
	Verification that the water system is being controlled to the lowest possible pressure while still meeting design loads, less diversity.  This shall include a review of TAB methods, control setpoints established by TAB and a physical verification of at least one leg from the pump to the coil having all balancing valves wide open and that during full cooling the cooling coil valve of that leg is 90% or more open.
	Demonstration
	


1Failure of an item is defined as follows:  


For air flow of supply and return:  a deviation of more than 10% of instrument reading 


For minimum outside air flow:  20% of instrument reading (30% for reading at intermediate supply flow for inlet vane or VFD OSA compensation system using linear proportional control)



For temperatures:  a deviation of more than 1(F



For air and water pressures:  a deviation of more than 10% of full scale of test instrument reading



For sound pressures:  a deviation of more than 3 decibels.  (Variations in background noise must be considered)

2Examples of a “system” are:   the air distribution system served by one air handler or the hydronic chilled water supply system served by a chiller or the condenser water system.  Systems can be defined smaller if inaccuracies in TAB work within the smaller defined system will have little or no impact on connected systems.

3Cooling season, Heating season or Both.  “Design” means within 5(of season design (ASHRAE 2 1/2%), or 95% of loading design.  A blank cell denotes no special seasonal test is required and that test can be executed during any season, if condition simulation is appropriate.


F.
Special Procedures  (other equipment to test with, etc.; reference to function ID)



None


G.
Required Monitoring  



None


I.
Acceptance Criteria  (referenced by function or mode ID)



Provided in footnote to test table above.


J.
Sampling Strategy for Identical Units



Described in test table above.

END OF SECTION 15050
COMMISSIONING

15350 – 2

