TESTING AND BALANCING OF AIR AND HYDRONIC SYSTEMS
Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical specifications

SECTION 15850 - TESTING AND BALANCING OF AIR AND HYDRONIC SYSTEMS

PART 1 - GENERAL

1.1
DESCRIPTION

A. The Contractor shall furnish all labor, equipment and services necessary for and incidental to Air and Water Systems Testing and Balancing.

B. The Contractor shall procure the services of an independent testing and balancing agency. The Testing and Balancing Agency (TBA)  specializes in testing and balancing of heating, ventilating, air-moving equipment, air-conditioning system and Hydronic systems.  The Mechanical Contractor shall award the test and balance contract to the above agency as soon as possible after receipt of contract.  

C. Testing and Balancing shall not begin until the systems have been completed and are in full working order.

D. Shop drawings must be provided to the TAB firm no later than 30 days after the final, approved shop drawings have been returned by the Architect to the Contractor.

E. Duct leakage testing shall be the responsibility of the TBA subcontractor.

F. Fire and smoke damper testing shall be done by the contractor and witnessed by the TAB firm. 

G. The final and complete Test and Balance Report shall be submitted, for approval, not less than two weeks before a final inspection of the Project is requested by the General Contractor. Failure to provide the Report shall be cause to delay the final inspection until the Report is Approved . 

H. Contractor is cautioned that test and Balance Report shall include both Grille counts, and Supply, Return, Outside Air and Exhaust Duct Traverses so that duct leakage can be calculated.

1.2
REFERENCES

A. AABC – National Standards for Total System Balance.

B. NEBB – Procedural Standards for Testing, Adjusting, and Balancing.

1.3
SUBMITTALS

A. Field Reports: Indicate deficiencies in systems that would prevent proper testing, adjusting, and balancing of systems and equipment to achieve specified performance.

B. Submit draft copies of report for review prior to final acceptance of Project. Provide final copies for Architect/Engineer and for inclusion in operating and maintenance manuals.

C. Provide reports in soft cover, letter size, binder manuals, complete with index page and indexing tabs, with cover identification at front and side. Include set of reduced drawings with air outlets and equipment identified to correspond with data sheets, and indicating, thermostat locations.

1.4
QUALITY ASSURANCE

A.
Perform total system balance in accordance with AABC National Standards for Field Measurement and Instrumentation, Total System Balance or NEBB Standards – Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems or Testing Adjusting and Balancing Bureau (TABB)-National Standards for Environmental Systems Balance.

1.5
QUALIFICATIONS 

A.
TBA shall be a Company specializing in the testing, adjusting, and balancing of systems specified in this Section with minimum three years experience.

PART 2 - PRODUCTS

2.1  
ADJUSTMENT DEVICES

A.
Replacement of adjustable pulleys, additional balancing dampers, additional fan belts, pressure taps and fitting, hydronic balancing valves and any other devices or equipment required to effect proper testing, adjusting and balancing shall be provided shall be provided by the Contractor at no additional cost to the Owner.

PART 3 - EXECUTION 

3.1
EXAMINATION 

A. Verify that systems are complete and operable before commencing work. Ensure the following conditions:

1. Systems are started and operating in a safe and normal condition.

2. Temperature control systems are installed complete and operable.

3. Proper thermal overload protection is in place for electrical equipment.

4. Final filters are clean and in place. If required, install temporary media in addition to final filters.

5. Duct systems are clean of debris.

6. Fans are rotating correctly.

7. Fire and volume dampers are in place and open.

8. Air coil fins are cleaned and combed.

9. Access doors are closed and duct end caps are in place.

10. Air outlets are installed and connected.

11. Duct system leakage is minimized.

12. Hydronic systems are flushed, filled, and vented.

13. Pumps are rotating correctly.

14. Proper strainer baskets are clean and in place.

15. Service and balance valves are open.

B. Beginning of work means acceptance of existing HVAC conditions.

3.2
INSTALLATION TOLERANCES

A. Air Handling Systems: Adjust to within plus or minus 5 percent of design for supply systems and plus or minus 5 percent of design for return and exhaust systems.

B. Air Outlets and Inlets; Adjust total to within plus 5 percent and minus 5 percent of design to space. Adjust outlets and inlets in space to within plus or minus 5 percent of design.

C. Hydronic Systems: Adjust to within plus or minus 5 percent of design.

3.3
ADJUSTING – GENERAL

A. Ensure recorded data represents actual measured or observed conditions.

B. Permanently mark setting of valves, dampers, and other adjustment devices allowing setting to be restored. Set and lock memory stops.

C. After adjustment, take measurement to verify balance has not been disrupted or that such disruption has been rectified.

D. Leave systems in proper working order, replacing belt guards, closing access doors, closing doors to electrical switch boxes, and restoring thermostats to specified settings.

E. At the time of final inspection the TAB agency may be required to recheck, in the presence of the Owner’s Representative, specific and random selections of data, air quantities, and air motion recorded in the certified report.  Points and areas for recheck shall be selected by the Architect.  Measurements and test procedures shall be the same as approved for the initial work for the certified report.  Selections for recheck, specific plus random, shall not exceed 10% of the total number tabulated in the report.

3.4
AIR SYSTEMS PROCEDURE ( MINIMUM REQUIREMENTS )
A. Test and adjust fan RPM to design requirements.

B. Test and record motor full load nameplate rating and actual ampere draw.

C. Test and record system static pressures, fan suction and discharge.

D. Adjust all main supply and return air duct to proper design CFM.

E. Test and adjust each diffuser, grille and register (new and existing as indicated on drawings). Reading and tests of diffusers, grilles and registers shall include design velocity (FPM) and as adjusted velocity, design CFM and adjusted CFM.

F. Test and record outside, mixed air and discharge temperatures (D.B. for heating cycle, D.B. and W.B. for cooling cycle).

G. In coordination with the ATC contractor, set adjustments of automatically operated dampers to operate as specified, indicated and/or noted.

H. Test and adjust air handling and distribution systems to provide required or design supply, return, outside and exhaust air quantities.

I. Make air quantity measurements in ducts by Pitot tube traverse of entire cross sectional area of duct.

J. Measure air quantities at air inlets and outlets.

K. Adjust distribution system to obtain uniform space temperatures free from objectionable drafts and noise.

L. Use volume control devices to regulate air quantities only to extend that adjustments do not create objectionable air motion or sound levels. Effect volume control by duct internal devices such as dampers and splitters.

M. Vary total system air quantities by adjustment of fan speeds. Provide drive changes required. Vary branch air quantities by damper regulation.

N. Provide system schematic with required and actual air quantities recorded at each outlet or inlet

O. Measure static air pressure conditions on air supply units, including filter and coil pressure drops, and total pressure across the fan. Make allowances for 50 percent loading of filters.

P. Adjust outside air automatic dampers, outside air, return air and exhaust dampers for design conditions.

Q. Measure temperature conditions across air, return air, and exhaust dampers to check leakage.

R. Where modulating dampers are provided, take measurement and balance at extreme conditions.

S. Measure and record pressure differentials between designated spaces. 

3.5
WATER SYSTEM PROCEDURE ( MINIMUM  REQUIREMENTS )
A. Prepare itemized equipment schedules, listing all cooling elements and equipment in the systems to be balanced. List in order on equipment schedules, by pump or zone according to the design, all cooling elements, all zone balancing valves, circuit pump and ending with the last items of equipment or transfer element in the respective zone or circuit. Include on schedule sheet column titles listing the location, type of element or apparatus, design conditions and measured conditions. Prepare individual pump report sheets for each zone or circuit.

B. Adjust water systems (as indicated on drawings) to provide required or design quantities.

C. Use calibrated Venturi tubes, orifices, or other metered fitting and pressure gages to determine flow rates for system balance. Where flow-metering devices are not installed, base flow balance on temperature difference across various heat transfer elements in the system.

D. Adjust systems to provide specified pressure drops and flows through heat transfer elements prior to thermal testing. Perform balancing by measurement of temperature differential in conjunction with air balancing.

E. Effect system balance with automatic control valves fully open to heat transfer elements.

F. Effect adjustment of water distribution systems by means of balancing cocks, valves, and fittings. Do not use service or shut-off valves for balancing unless indexed for balance point.

G. Test pumps and adjust flow. Record the following on pumps report sheets: (a) suction and discharge pressure, (b) running amps and brake horsepower of pump motor under full flow and no flow conditions, (c) pressure drop across pump in feet of water and total GMP pump is handling under full flow conditions.

H. Where available pump capacity is less than total flow requirements or individual system parts, full flow in one part may be simulated by temporary restriction of flow to other parts.

3.6
REQUIRED REPORTS TO BE SUBMITTED
A.
The following reports shall be submitted, as a minimum, with a complete Title Page, Summary , and Instrument List. All data and nomenclature shall be provided, as required by AABC and/or NEBB Procedure manuals, for each device tested and balanced.

1.
Electric Motors.

2.
V-Belt Motors.

3.
VFD Drives.

4.
Pump Data.

5. 
Heating and Cooling Coils Data.

6. 
Air Moving Equipment.

7.
Return Air/ Outside Air Data.

8.
Exhaust Air Data.

9. 
Duct Traverses.

10.
Air Distribution Test Sheets.

3.7
COMMISSIONING

A.
Balancing Agency shall coordinate with the Mechanical Contractor the Commissioning requirements as here-in-before specified. 

B.
Contractor is cautioned that the Owner, thru the Architect, reserves the right to check and verify any and all points and readings of the Test and Balance report. If 15% or more of the points do not agree with the report, then the Contractor shall re-test and re-balance the entire project and submit a complete new Report. If 15% or more of this new Data is independently verified and still does not agree with the Contractor’s new Report, then the Owner has the right to hire an Independent Test and Balance Contractor and the Original Contractor shall be held responsible to pay these costs.

C.  
All TAB deficiencies shall be corrected when found.  Any deficiencies that are (for whatever reason) not corrected immediately shall be shown in the TAB report and listed on a summary sheet in the front of the TAB report.  The TAB report must be completed and accepted by the Mechanical Engineer before the project is accepted and all items on the summary sheet shall become punch list items with dollar values assigned to them.

END OF SECTION 15850
Section 15850 - Page 6
TESTING AND BALANCING OF AIR AND HYDRONIC SYSTEMS
15850 – 1

