Copyright 2000 and 2005 AIA
MASTERSPEC Full Length
11/00 (R 05/05)

Copyright 2000 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 070150.19 - PREPARATION FOR RE-ROOFING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Roof tear-off.

2. Partial roof tear-off.

3. Temporary roofing membrane.

4. Roof re-cover preparation.

5. Removal of base flashings.

6. Protection of existing roofing system that is not reroofed.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 01 Section "Summary" for use of the premises and phasing requirements.

2. Division 01 Section "Summary" for restrictions on use of the premises due to Owner or tenant occupancy.

3. Division 01 Section "Construction Progress Documentation" for photographs taken before reroofing preparation.

Retain subparagraph above or first subparagraph below, or delete both if not required.

4. Division 01 Section "Photographic Documentation" for photographs taken before reroofing preparation.

5. Division 01 Section "Temporary Facilities and Controls" for temporary construction and environmental-protection measures for reroofing preparation.

6. Division 01 Section "Cutting and Patching" for cutting and patching procedures for reroofing preparation.

7. Division 03 Section "Cast-in-Place Concrete" for concrete deck replacement.

8. Division 03 Section "Maintenance of Cast-in-Place Concrete" for concrete deck patching and repairs.

9. Division 05 Section "Steel Decking" for steel deck replacement.

10. Division 06 Section "[Rough Carpentry] [Miscellaneous Rough Carpentry]" for wood nailers, cants, curbs, and blocking [parapet sheathing] [and] [wood deck panel replacement].

11. Division 07 Section "<Insert Section title for type of membrane roofing system>" for roofing membrane, base flashings, [substrate boards,] [roof insulation,] [cover boards,] and roofing accessories.

12. Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

13. Division 07 Section "Roof Specialties."

14. Division 07 Section "Manufactured Roof Expansion Joints."

15. Division 22 Section "Storm Drainage Piping Specialties" for replacement roof drains.

16. Division 23 Sections for HVAC equipment removal and reinstallation.

17. Division 26 Sections for electrical equipment disconnection and reconnection.

Allowances and unit prices may be required in Bid Documents.  Examples of allowances and unit prices might include removal and replacement of wet roof insulation, deteriorated deck, wood nailers, curbs, cants, and deteriorated parapet sheathing that may be discovered during demolition of an existing roofing system.  Revise paragraphs below if further description is required.

C. Allowances:  Refer to Division 01 Section "Allowances" for description of Work in this Section affected by allowances.

D. Unit Prices:  Refer to Division 01 Section "Unit Prices" for description of Work in this Section affected by unit prices.

1.3 MATERIALS OWNERSHIP

A. Except for items or materials indicated to be reused, reinstalled, or otherwise indicated to remain Owner's property, demolished materials shall become Contractor's property and shall be removed from Project site.

1.4 DEFINITIONS

Retain definitions and terms that remain after this Section has been edited.

A. Roofing Terminology:  Refer to ASTM D 1079 and glossary in NRCA's "The NRCA Roofing and Waterproofing Manual" for definition of terms related to roofing work in this Section.

Description in first paragraph below is of a conventional membrane roofing system.  Revise to include more details of existing roofing system or to describe components of an existing protected membrane roofing system or coated foamed roofing if applicable.

B. Existing Membrane Roofing System:  [Built-up asphalt] [Built-up coal-tar] [EPDM] [CSPE] [PVC] [TPO] [APP-modified bituminous] [SBS-modified bituminous] roofing membrane, surfacing, and components and accessories between deck and roofing membrane.

C. Substrate Board:  Rigid board or panel products placed over the roof deck that serve as thermal barriers, provide a smooth substrate, or serve as a component of a fire-resistance-rated roofing system.

D. Roof Re-Cover Preparation:  Existing roofing membrane that is to remain and be prepared for reuse.

E. Roof Tear-Off:  Removal of existing membrane roofing system from deck.

F. Partial Roof Tear-Off:  Removal of a portion of existing membrane roofing system from deck or removal of selected components and accessories from existing membrane roofing system.

G. Remove:  Detach items from existing construction and legally dispose of them off-site unless indicated to be removed and reinstalled.

H. Existing to Remain:  Existing items of construction that are not indicated to be removed.

1.5 SUBMITTALS

A. Product Data:  For each type of product indicated.

Retain paragraph below if Contractor may propose, or is required to propose, temporary roofing.  Usually delete submittal if temporary roofing is specified in the Section Text.

B. Temporary Roofing:  Include Product Data and description of temporary roofing system.  If temporary roof will remain in place, submit surface preparation requirements needed to receive permanent roof, and submit a letter from roofing membrane manufacturer stating acceptance of the temporary membrane, and that its inclusion will not adversely affect the roofing system's resistance to fire and wind[ or its FMG rating].

Retain first paragraph below if mechanically fastening recover board or components of new membrane roofing system.

C. Fastener pull-out test report.

D. Photographs or Videotape:  Show existing conditions of adjoining construction and site improvements, including exterior and interior finish surfaces, that might be misconstrued as having been damaged by reroofing operations.  Submit before Work begins.

Retain records submittal in paragraph below if applicable.  Landfill records may be required by Owner when discarded roofing materials contain hazardous wastes.

E. Landfill Records:  Indicate receipt and acceptance of hazardous wastes, such as asbestos-containing material, by a landfill facility licensed to accept hazardous wastes.

Coordinate below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

F. Qualification Data:  For Installer[ including certificate that Installer is licensed to perform asbestos abatement] [and] [is approved by warrantor of existing roofing system].

1.6 QUALITY ASSURANCE

Retain first option in first paragraph below if asbestos-containing material is present or could be present and a licensed contractor is required.  Retain second option if existing roof is to remain, is warrantied, and will be worked on.

A. Installer Qualifications:  Installer of new membrane roofing system[, licensed to perform asbestos abatement in the State or jurisdiction where Project is located] [and] [approved by warrantor of existing roofing system to work on existing roofing].

B. Regulatory Requirements:  Comply with governing EPA notification regulations before beginning membrane roofing removal.  Comply with hauling and disposal regulations of authorities having jurisdiction.

Consider a preliminary reroofing conference if Project is large or complex.  This conference would precede the reroofing conference.

C. Preliminary Reroofing Conference:  Conduct conference at Project site to comply with requirements in Division 01 Section "Project Management and Coordination."  Review methods and procedures related to roofing system including, but not limited to, the following:

Delete subparagraphs below not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.  Coordinate with preliminary and preinstallation conference requirements in replacement membrane roofing system Section.

1. Meet with Owner; Architect; Owner's insurer if applicable; testing and inspecting agency representative; roofing system manufacturer's representative; deck Installer; roofing Installer including project manager, superintendent, and foreman; and installers whose work interfaces with or affects reroofing including installers of roof accessories and roof-mounted equipment.

2. Review methods and procedures related to reroofing preparation, including membrane roofing system manufacturer's written instructions.

3. Review temporary protection requirements for existing roofing system that is to remain, during and after installation.

4. Review roof drainage during each stage of reroofing and review roof drain plugging and plug removal procedures.

5. Review and finalize construction schedule, and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

6. Review existing deck removal procedures and Owner notifications.

7. Review procedures to determine condition and acceptance of existing deck and base flashing substrate for reuse.

8. Review structural loading limitations of deck during reroofing.

9. Review base flashings, special roofing details, drainage, penetrations, equipment curbs, and condition of other construction that will affect reroofing.

10. Review HVAC shutdown and sealing of air intakes.

11. Review shutdown of fire-suppression, -protection, and -alarm and -detection systems.

12. Review procedures for asbestos removal or unexpected discovery of asbestos-containing materials.

13. Review governing regulations and requirements for insurance and certificates if applicable.

14. Review existing conditions that may require notification of Architect before proceeding.

A reroofing conference is recommended before starting.

D. Reroofing Conference:  Conduct conference at Project site to comply with requirements in Division 01 Section "Project Management and Coordination."  Review methods and procedures related to roofing system including, but not limited to, the following:

Delete subparagraphs below not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.  Coordinate with preliminary and preinstallation conference requirements in replacement membrane roofing system Section.

1. Meet with Owner; Architect; Owner's insurer if applicable; testing and inspecting agency representative; roofing system manufacturer's representative; deck Installer; roofing Installer including project manager, superintendent, and foreman; and installers whose work interfaces with or affects reroofing including installers of roof accessories and roof-mounted equipment.

2. Review methods and procedures related to reroofing preparation, including membrane roofing system manufacturer's written instructions.

3. Review temporary protection requirements for existing roofing system that is to remain, during and after installation.

4. Review roof drainage during each stage of reroofing and review roof drain plugging and plug removal procedures.

5. Review and finalize construction schedule, and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

6. Review existing deck removal procedures and Owner notifications.

7. Review procedures to determine condition and acceptance of existing deck for reuse.

8. Review structural loading limitations of deck during reroofing.

9. Review base flashings, special roofing details, drainage, penetrations, equipment curbs, and condition of other construction that will affect reroofing.

10. Review HVAC shutdown and sealing of air intakes.

11. Review shutdown of fire-suppression, -protection, and -alarm and -detection systems.

12. Review procedures for asbestos removal or unexpected discovery of asbestos-containing materials.

13. Review governing regulations and requirements for insurance and certificates if applicable.

14. Review existing conditions that may require notification of Architect before proceeding.

1.7 PROJECT CONDITIONS

Retain, revise, or delete paragraphs and subparagraphs in this Article to suit Project.  Add other limitations if necessary, such as when adjacent floors will be occupied.

A. Owner will occupy portions of building immediately below reroofing area.  Conduct reroofing so Owner's operations will not be disrupted.  Provide Owner with not less than [72] <Insert number> hours' notice of activities that may affect Owner's operations.

1. Coordinate work activities daily with Owner so Owner can place protective dust or water leakage covers over sensitive equipment or furnishings, shut down HVAC and fire-alarm or -detection equipment if needed, and evacuate occupants from below the work area if desired.

Delete subparagraph below if no known impaired deck areas or if special protection is provided below the work area.

2. Before working over structurally impaired areas of deck, notify Owner to evacuate occupants from below the affected area.  Verify that occupants below the work area have been evacuated prior to proceeding with work over the impaired deck area.

B. Protect building to be reroofed, adjacent buildings, walkways, site improvements, exterior plantings, and landscaping from damage or soiling from reroofing operations.

C. Maintain access to existing walkways, corridors, and other adjacent occupied or used facilities.

D. Owner assumes no responsibility for condition of areas to be reroofed.

Retain subparagraph below and revise to suit Project.

1. Conditions existing at time of inspection for bidding will be maintained by Owner as far as practical.

Retain paragraph below if limiting construction loads on existing roof deck and building structure.  Verify load limit combinations with structural engineer and insert maximum wheel loads (concentrated point loads) and maximum distributed loads for stored or demolished materials.  Revise to suit Project.

E. Limit construction loads on roof to <Insert load> rooftop equipment wheel loads and <Insert load> for uniformly distributed loads.

Retain first three paragraphs below if applicable.

F. A roof moisture survey of existing membrane roofing system is available for Contractor's reference.

G. The results of an analysis of test cores from existing membrane roofing system are available for Contractor's reference.

H. Construction Drawings[ and Project Manual] for existing roofing system are provided for Contractor's reference.  Contractor is responsible for conclusions derived from existing documents.

I. Weather Limitations:  Proceed with reroofing preparation only when existing and forecasted weather conditions permit Work to proceed without water entering into existing roofing system or building.

Retain one of two paragraphs and associated subparagraphs below or delete if no hazardous materials.  Asbestos-containing materials may be encountered during reroofing.  Coordinate statements with the General and Supplementary Conditions.

J. Hazardous Materials:  It is not expected that hazardous materials such as asbestos-containing materials will be encountered in the Work.

1. Hazardous materials will be removed by Owner before start of the Work.  Existing roof will be left no less watertight than before removal.

Retain subparagraph below to cover instances where hazardous materials are unexpectedly found and must be remediated.

2. If materials suspected of containing hazardous materials are encountered, do not disturb; immediately notify Architect and Owner.  Hazardous materials will be removed by Owner under a separate contract.

Retain paragraph and subparagraphs above and delete paragraph and subparagraphs below if asbestos is present and Owner has a separate contract to abate asbestos before reroofing preparation begins.

Retain below and delete above if asbestos abatement is part of the Work of this Contract.  Consult a professional liability insurance carrier for current recommendations.  Indemnification and a waiver of claims may be required from Owner as a condition for providing services related to asbestos abatement.

K. Hazardous Materials:  Present in building to be reroofed.  A report on the presence of hazardous materials is on file for review and use.  Examine report to become aware of locations where hazardous materials are present.

1. Hazardous material remediation is specified elsewhere in the Contract Documents.

2. Do not disturb hazardous materials or items suspected of containing hazardous materials except according to procedures specified elsewhere in the Contract Documents.

3. Coordinate with hazardous material remediation Contractor to prevent water from entering building or existing roofing system.

1.8 WARRANTY

Retain this Article if portions of existing roof are to remain or if an adjoining existing roof is under warranty.

A. Existing Warranties:  Remove, replace, patch, and repair materials and surfaces cut or damaged during reroofing, by methods and with materials so as not to void existing roofing system warranty.  Notify warrantor before proceeding.

1. Notify warrantor of existing roofing system on completion of reroofing, and obtain documentation verifying that existing roofing system has been inspected and warranty remains in effect.  Submit documentation at Project closeout.

PART 2 -  PRODUCTS

2.1 INFILL MATERIALS

Delete this Article if no infill materials will be required or anticipated.

A. Use infill materials matching existing membrane roofing system materials, unless otherwise indicated.

Roofing system infill materials, such as substrate boards, insulation, cover boards, insulation fasteners, and performance and installation options, have been included in the applicable membrane roofing Section.

1. Infill materials are specified in Division 07 Section "<Insert Section title of applicable membrane roofing Section>."

2.2 TEMPORARY ROOFING MATERIALS

Delete this Article if temporary roofing is not required.

If choice of temporary roofing materials is left to Contractor, retain paragraph below and delete remainder of this Article.

A. Selection of materials and design of temporary roofing is responsibility of Contractor.

Retain applicable paragraphs below for temporary roofing materials.  Materials are examples only.  Material selection may depend on type of replacement insulation, roofing membrane, and final disposition of temporary roofing.  Temporary roofing is either removed or permanently incorporated into membrane roofing system as a vapor retarder.

Sheathing paper may be required as a slip sheet over wood-plank decks, usually under a base sheet.  Delete paragraph below if no wood-plank decks or if not required by manufacturer's specifications.

B. Sheathing Paper:  Red-rosin type, minimum 3 lb/100 sq. ft. (0.16 kg/sq. m).

Retain paragraph below if base sheet is used as foundation sheet of two-ply temporary roofing.

C. Base Sheet:  ASTM D 4601, Type II, nonperforated, asphalt-impregnated and -coated, glass-fiber sheet.

Retain paragraph below for second ply or both plies of two-ply temporary roofing.

D. Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.

Retain first paragraph below if priming concrete deck before placing temporary roofing.

E. Asphalt Primer:  ASTM D 41.

F. Roofing Asphalt:  ASTM D 312, Type III or IV.

2.3 RECOVER BOARDS

Select one of four recover boards below if required or delete this Article.  Recover boards provide a smooth substrate and separate existing roofing membrane from new roofing membrane.  Selections in paragraphs below are limited to thin layers offering little insulation.  Roof insulation that may also serve as a recover board is specified in various Division 07 Sections for membrane roofing systems.

A. Recover Board:  ASTM C 208, Type II, Grade [1] [2], cellulosic-fiber insulation board; 1/2 inch (13 mm) thick.

B. Recover Board:  Fan-folded, unfaced, extruded-polystyrene board insulation; nominal thickness [3/16 inch (5 mm)] [1/4 inch (6 mm)] [3/8 inch (10 mm)].

C. Recover Board:  ASTM C 1177/C 1177M, glass-mat, water-resistant gypsum substrate; [1/4 inch (6 mm)] [1/2 inch (13 mm)] [Type X, 5/8 inch (16 mm)] thick.

D. Recover Board:  ASTM C 728, perlite board; [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)] thick.

Retain below with recover board selected from paragraphs above.

E. Fasteners:  Factory-coated steel fasteners, No. [12] [or] [14], and metal or plastic plates listed in FMG's "Approval Guide," designed for fastening recover boards to deck.

2.4 AUXILIARY REROOFING MATERIALS

A. General:  Auxiliary reroofing preparation materials recommended by roofing system manufacturer for intended use and compatible with components of [existing and ]new membrane roofing system.

B. Base Sheet Fasteners:  Capped head, factory-coated steel fasteners, listed in FMG's "Approval Guide."

C. Metal Flashing Sheet:  Metal flashing sheet is specified in Division 07 Section "Sheet Metal Flashing and Trim."

PART 3 -  EXECUTION

3.1 PREPARATION

Retain paragraph and subparagraphs below if portions of roof area that are to remain unaltered and in-service during the Work require protection.  Typically retain if reroofing work is carried out on or above existing roof that is to remain and there is a possibility of items falling on roof below.

A. Protect existing membrane roofing system that is indicated not to be reroofed.

Retain first subparagraph below, which is an example only, if prescribing materials to be used as protection.  Delete or revise to suit Project.  If existing membrane roofing system that is to remain is under warranty, revise to add warrantor's protection requirements.

1. Loosely lay 1-inch- (25-mm-) minimum thick, molded expanded polystyrene (MEPS) insulation over the roofing membrane in areas indicated.  Loosely lay 15/32-inch (12-mm) plywood or OSB panels over MEPS.  Extend MEPS past edges of plywood or OSB panels a minimum of 1 inch (25 mm).

2. Limit traffic and material storage to areas of existing roofing membrane that have been protected.

3. Maintain temporary protection and leave in place until replacement roofing has been completed.

Depending on duration of equipment shutdown and occupancy of building, revise paragraph below if necessary to specify special work hours (e.g., nights, weekends, etc.) for portions of roof near air intakes.  If necessary to deactivate all or a portion of fire-detection system, revise below to add special measures such as a fire watch.

B. Coordinate with Owner to shut down air intake equipment in the vicinity of the Work.  Cover air intake louvers before proceeding with reroofing work that could affect indoor air quality or activate smoke detectors in the ductwork.

Delete paragraph below if existing roofing membrane and base flashings are to remain.

C. During removal operations, have sufficient and suitable materials on-site to facilitate rapid installation of temporary protection in the event of unexpected rain.

Delete first paragraph and subparagraph below if no roof drains.

D. Maintain roof drains in functioning condition to ensure roof drainage at end of each workday.  Prevent debris from entering or blocking roof drains and conductors.  Use roof-drain plugs specifically designed for this purpose.  Remove roof-drain plugs at end of each workday, when no work is taking place, or when rain is forecast.

1. If roof drains will be temporarily blocked or unserviceable due to roofing system removal or partial installation of new membrane roofing system, provide alternative drainage method to remove water and eliminate ponding.  Do not permit water to enter into or under existing membrane roofing system components that are to remain.

E. Verify that rooftop utilities and service piping have been shut off before commencing Work.

3.2 ROOF TEAR-OFF

Retain option in paragraph below if Owner intends to authorize each day's work.  Specify restrictions or limitations that will be placed on Installer to limit unscheduled delays.

A. General:  Notify Owner each day of extent of roof tear-off proposed[ and obtain authorization to proceed].

Retain paragraph below for existing aggregate-ballasted elastomeric or thermoplastic membrane roofing systems or for aggregate-surfaced foamed roofing.  Retain option or revise to suit Project.

B. Remove aggregate ballast from roofing membrane.[ Store aggregate ballast for reuse].

Retain paragraph below for existing aggregate-surfaced built-up bituminous roofing.

C. Remove loose aggregate from aggregate-surfaced built-up bituminous roofing with a power broom.

Retain paragraph below if applicable.  Retain option or revise to suit Project.

D. Remove pavers from roofing membrane.[ Store and protect pavers for reuse.  Discard cracked pavers].

Retain paragraph and subparagraphs below for protected membrane roofing.

E. Remove protection mat and extruded-polystyrene insulation from protected membrane roofing.

1. Discard extruded-polystyrene insulation that is wet and exceeds 8 lb/cu. ft. (128 kg/cu. m).

2. Store extruded-polystyrene insulation for reuse and protect from physical damage.

Retain paragraph and applicable subparagraphs below for roof tear-off.

F. Roof Tear-Off:  Remove existing roofing membrane and other membrane roofing system components down to the deck.

1. Remove [cover boards] [roof insulation] [and] [substrate boards].

Retain subparagraph below if applicable.

2. Bitumen and felts that are firmly bonded to concrete decks are permitted to remain if felts are dry.  Remove unadhered bitumen and felts and wet felts.

FMG limits the quantity of asphalt permitted to remain on steel decks.  Retain subparagraph below if applicable.

3. Remove excess asphalt from steel deck.  A maximum of 15 lb/100 sq. ft. (0.72 kg/sq. m) of asphalt is permitted to remain on steel decks.

In subparagraph below, delete option for cutting off fasteners if roofing membrane will be placed directly over the deck.  If fastener removal is difficult, consider placing recover boards over the deck and cutting fasteners above the deck surface rather than removing them.  If cut fasteners can fall from deck, specify fastener removal.

4. Remove fasteners from deck[ or cut fasteners off slightly above deck surface].

Retain paragraph and applicable subparagraphs below if tear-off is limited to partial areas of roof but not entire area of existing membrane roofing system down to the deck.

G. Partial Roof Tear-Off:  Where indicated, remove existing roofing membrane and other membrane roofing system components down to the deck.

1. Remove [cover boards] [roof insulation] [and] [substrate boards].

Retain subparagraph below if applicable.

2. Bitumen and felts that are firmly bonded to concrete decks are permitted to remain if felts are dry.  Remove unadhered bitumen and felts and wet felts.

Retain subparagraph below if applicable.  FMG limits the quantity of asphalt permitted to remain on steel decks.  Revise below to include weight of asphalt revealed by test cores or test cuts if available.

3. Remove excess asphalt from steel deck.  A maximum of 15 lb/100 sq. ft. (0.72 kg/sq. m) of asphalt is permitted to remain on steel decks.

In subparagraph below, delete option for cutting off fasteners if roofing membrane will be placed directly over the deck.  If fastener removal is difficult, consider placing recover boards over the deck and cutting fasteners above the deck surface rather than removing them.  If cut fasteners can fall from deck, specify fastener removal.

4. Remove fasteners from deck[ or cut fasteners off slightly above deck surface].

Retain paragraph and applicable subparagraphs below if partial roof tear-off is limited to removing existing roofing membrane and selected components within membrane roofing system that have been identified for removal.  Other components may include wet cover boards, roof insulation, and substrate boards.

H. Partial Roof Tear-Off:  Remove existing roofing membrane and immediately check for presence of moisture by visually observing [cover boards] [roof insulation] [substrate boards] that will remain.

1. Coordinate with Owner's inspector to schedule times for tests and inspections immediately after membrane removal.

Retain subparagraph above and delete subparagraph below if checking will be performed by Owner's inspector.

2. With an electrical capacitance moisture-detection meter, spot check [cover boards] [roof insulation] [substrate boards] that will remain.

Revise subparagraph below to add further qualifications or criteria to determine whether insulation, cover boards, and substrate boards are too wet.  Retain option if removal is not anticipated in the Contact Documents and revise if applicable.

3. Remove wet or damp boards and roof insulation.[ Removal will be paid for by adjusting the Contract Sum according to unit prices included in the Contract Documents.]

Retain subparagraph below if applicable.

4. Bitumen and felts that are firmly bonded to concrete decks are permitted to remain if felts are dry.  Remove unadhered bitumen and felts and wet felts.

FMG limits the quantity of asphalt permitted to remain on steel decks.  Retain subparagraph below if applicable.

5. Remove excess asphalt from steel deck.  A maximum of 15 lb/100 sq. ft. (0.72 kg/sq. m) of asphalt is permitted to remain on steel decks.

Delete option below for cutting off fasteners if roofing membrane will be placed directly over the deck.  If fastener removal is difficult, consider placing recover boards over the deck and cutting fasteners above the deck surface rather than removing them.  If cut fasteners can fall from deck, specify fastener removal.

6. Remove fasteners from deck[ or cut fasteners off slightly above deck surface].

3.3 DECK PREPARATION

Retain this Article for roof tear-off or partial roof tear-off.

A. Inspect deck after[ partial] tear-off of membrane roofing system.

Delete subparagraph below if deck is not concrete.

1. Verify that concrete substrate is visibly dry and free of moisture.  Test for capillary moisture by plastic sheet method according to ASTM D 4263 or by pouring 1 pint (0.5 L) of hot roofing asphalt on deck at start of each day's work and at start of each roof area or plane.  Do not proceed with roofing work if moisture condenses under the plastic sheet or if asphalt test sample foams or can be easily and cleanly stripped after cooling.

Delete first paragraph below if deck is cast-in-place concrete.

B. If broken or loose fasteners that secure deck panels to one another or to structure are observed, or if deck appears or feels inadequately attached, immediately notify Architect.  Do not proceed with installation until directed by Architect.

C. If deck surface is not suitable for receiving new roofing, or if structural integrity of deck is suspect, immediately notify Architect.  Do not proceed with installation until directed by Architect.

Retain paragraph below and revise to add fastening requirements if preferred.

D. Provide additional deck securement as indicated on Drawings.

Retain below and revise to include replacement criteria.  Coordinate specification of type of deck with "Related Sections" Paragraph in Part 1 "Summary" Article.

E. Replace deck as indicated on Drawings.  Replacement deck is specified in Division [03] [05] [06] Section "<Insert Section title>."

3.4 INFILL MATERIALS INSTALLATION

Delete this Article if not required.

A. Immediately after removal of selected portions of existing membrane roofing system, and inspection and repair, if needed, of deck, fill in the tear-off areas to match existing membrane roofing system construction.

1. Installation of infill materials is specified in Division 07 Section "<Insert Section title>."

2. Install new roofing membrane patch over roof infill area.  If new roofing membrane is installed the same day tear-off is made, roofing membrane patch is not required.

3.5 TEMPORARY ROOFING MEMBRANE

Delete this Article if not required.

Retain one of first two paragraphs below.  Retain first if Contractor proposes construction of temporary roofing membrane.  Retain second if Architect prescribes type of temporary roofing membrane.

A. Install approved temporary roofing membrane over area to be reroofed.

Retain paragraph below if built-up temporary roofing membrane is required.  Revise to suit Project if another membrane type is applicable.

B. Install temporary roofing membrane over area to be reroofed.  [Install 2 glass-fiber felts] [Mechanically fasten base sheet and install a glass-fiber felt] lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed glass-fiber felt in a solid mopping of hot roofing asphalt applied within equiviscous temperature range.  Glaze-coat completed surface with hot roofing asphalt.

Retain one of two paragraphs below.  Retain first if removal of temporary roofing membrane is required.  Retain second if temporary roofing membrane is to remain.

C. Remove temporary roofing membrane before installing new roofing membrane.

D. Prepare the temporary roof to receive new roofing membrane [according to approved temporary roofing membrane proposal] [by patching and repairing temporary roofing membrane] <Insert preparation method>.  Restore temporary roofing membrane to watertight condition.  Obtain approval for temporary roof substrate from membrane manufacturer and Architect prior to installation of new roof.

3.6 ROOF RE-COVER PREPARATION

Retain this Article if Project is a roof re-cover of an existing roofing membrane.  Retain paragraphs that apply to type of new and existing roofing membrane.

Retain paragraph and subparagraphs below for new built-up and modified bituminous roofing or for fully adhered elastomeric and thermoplastic roofing membranes over existing built-up and modified bituminous roofing, elastomeric and thermoplastic roofing membranes, or coated foamed roofing.  Delete option if not required.  Most mechanically attached roofing membranes do not have buttons projecting above the membrane.

A. Remove blisters, ridges, buckles,[ mechanically attached roofing membrane fastener buttons projecting above the membrane,] and other substrate irregularities from existing roofing membrane that inhibit new recover boards from conforming to substrate.

Retain subparagraph below for existing aggregate-surfaced, built-up bituminous roofing.

1. Remove loose aggregate from aggregate-surfaced, built-up bituminous roofing with a power broom.

Retain first subparagraph below for existing coated foamed roofing.  Scarifying is usually needed to avoid development of birdbaths.

2. Scarify the surface of sprayed polyurethane foam as necessary to achieve a sufficiently uniform plane to receive new recover boards.

3. Broom clean existing substrate.

4. Coordinate with Owner's inspector to schedule times for tests and inspections before proceeding with installation of recover boards.

Retain subparagraph above and delete first subparagraph below if checking will be performed by Owner's inspector.

5. Verify that existing substrate is dry before proceeding with installation of recover boards.  Spot check substrates with an electrical capacitance moisture-detection meter.

6. Remove materials that are wet or damp.  Removal will be paid for by adjusting the Contract Sum according to unit prices included in the Contract Documents.

Retain paragraph and subparagraphs below for new mechanically fastened, ballasted, or protected elastomeric and thermoplastic roofing membranes over existing built-up and modified bituminous roofing, elastomeric and thermoplastic roofing membranes, or coated foamed roofing.  Delete options if not required.  Most mechanically attached roofing membranes do not have buttons projecting above the membrane.

Preparation method below permits two reroofing system alternatives:  One is to install a recover board between old and new roofing membranes; the other is to install a fleece-backed membrane directly over the existing roofing membrane.  For the fleece-backed alternative, coordinate with Division 07 Section for type of new membrane roofing system and specify a fleece-backed membrane manufactured for re-cover applications.  Verify that new roofing membrane will be compatible with existing roofing membrane.  For new modified bituminous roofing membrane or mechanically fastened elastomeric and thermoplastic roofing membranes, verify that existing roofing system has enough compressive resistance, or specify a recover board.

If existing roofing membrane is an aggregate-surfaced built-up membrane, specify a recover board rather than a fleece-backed roofing membrane.

If existing roofing system is coated foamed roofing without granules, aggregate, or sand in or on the coating, a new roofing membrane without a fleece backing can be installed directly over the coated foamed roofing.

B. Remove blisters, ridges, buckles,[ mechanically attached roofing membrane fastener buttons projecting above the membrane,] and other substrate irregularities from existing roofing membrane that inhibit new [recover boards] [roofing membrane] from conforming to substrate.

Retain subparagraph below for existing aggregate-surfaced, built-up bituminous roofing.

1. Remove loose aggregate from aggregate-surfaced, built-up bituminous roofing with a power broom.

Retain first subparagraph below for existing coated foamed roofing.  Scarifying is usually needed to avoid development of birdbaths.

2. Scarify the surface of sprayed polyurethane foam as necessary to achieve a sufficiently uniform plane to receive new [recover boards] [roofing membrane].

3. Broom clean existing substrate.

4. Coordinate with Owner's inspector to schedule times for tests and inspections.

Retain subparagraph above and delete first subparagraph below if checking will be performed by Owner's inspector.

5. Verify that existing substrate is dry before proceeding with installation.  Spot check substrate with an electrical capacitance moisture-detection meter.

6. Remove materials that are wet and damp.  Removal will be paid for by adjusting the Contract Sum according to unit prices included in the Contract Documents.

Retain one of two paragraphs and subparagraphs below for new coated foamed roofing over existing built-up and modified bituminous roofing, elastomeric and thermoplastic roofing membranes, or coated foamed roofing.  Delete options if not required.  Most mechanically attached roofing membranes do not have buttons projecting above the membrane.

C. Remove blisters and areas of membrane not fully adhered.

If existing roofing is an elastomeric or thermoplastic membrane, delete paragraph above and retain paragraph and subparagraphs below.  A recover board is needed over existing mechanically fastened and loosely laid elastomeric or thermoplastic roofing membranes because these membranes are not continuously attached.  A recover board is also needed over fully adhered elastomeric or thermoplastic roofing membranes to keep them from delaminating due to high heat during the foam curing process.

D. Remove[ mechanically attached roofing membrane fastener buttons projecting above the membrane and other] substrate irregularities that inhibit new recover boards from conforming to substrate.

Retain subparagraph below for existing aggregate-surfaced, built-up bituminous roofing.

1. Remove loose aggregate from aggregate-surfaced, built-up bituminous roofing with a power broom.

Delete subparagraph below if coated foamed roofing is applied to recover boards.

2. Clean substrate of contaminants such as dirt, debris, oil, and grease that can affect adhesion of coated foamed roofing.

Retain subparagraph below if existing roof is built-up or modified bituminous roofing.

3. Power vacuum the existing roof surface.  If recommended by foam manufacturer, prime dried surface at recommended rate with recommended primer.

Retain subparagraph below if existing roof is coated foamed roofing.

4. Scarify the surface of coated polyurethane roofing as necessary to achieve a suitable substrate for new roofing.

Retain first subparagraph and associated subparagraphs below if additional fastening of existing roofing system is required.  Numerous field-uplift tests should be made during design stage to determine if existing roofing system is adequately attached.  If attachment is inadequate, specify additional membrane fasteners or install a mechanically attached cover board.

5. Provide additional uplift securement for existing roofing system with new screws and plates applied to each roof zone at the following densities:

a. Field of roof, one fastener for each <Insert area>.

b. Corners of roof, one fastener for each <Insert area>.

c. Perimeters of roof, one fastener for each <Insert area>.  Width of perimeter zone of roof is <Insert dimension>.

6. Verify that surface is dry by pressing litmus paper to surface areas most likely to retain moisture, such as shaded areas and low spots.  If paper changes color, surface is too wet to apply foam.

7. Build-up isolated low spots on existing roofing membrane with sprayed foam specified in Division 07 Section "Coated Foamed Roofing" to prevent ponding.

3.7 EXISTING BASE FLASHINGS

A. Remove existing base flashings around parapets, curbs, walls, and penetrations.

1. Clean substrates of contaminants such as asphalt, sheet materials, dirt, and debris.

B. Do not damage metal counterflashings that are to remain.  Replace metal counterflashings damaged during removal with counterflashings [of same metal, weight or thickness, and finish.] [specified in Division 07 Section "Sheet Metal Flashing and Trim." ] [specified in Division 07 Section "Roof Specialties." ]

Retain paragraph below if existing parapet sheathing will be reused.

C. Inspect parapet sheathing for deterioration and damage.  If parapet sheathing has deteriorated, immediately notify Architect.

Retain below if replacing parapet sheathing.

D. Remove existing parapet sheathing and replace with new [pressure-preservative] [exterior fire-retardant]-treated plywood sheathing, [19/32 inch (15 mm)] <Insert thickness> thick.  If parapet framing has deteriorated, immediately notify Architect.

1. Plywood parapet sheathing is specified in Division 06 Section "[Rough Carpentry] [Miscellaneous Rough Carpentry]."

3.8 FASTENER PULL-OUT TESTING

A. [Perform] [Retain independent testing and inspecting agency to conduct] fastener pull-out tests according to SPRI FX-1, and submit test report to Architect before installing new membrane roofing system.

1. Obtain Architect's approval to proceed with specified fastening pattern.  Architect may furnish revised fastening pattern commensurate with pull-out test results.

3.9 RECOVER BOARD INSTALLATION

Retain this Article if recover boards will be installed over existing insulation or roofing membrane.

A. Install recover boards over [roof insulation] [roofing membrane] with long joints in continuous straight lines and end joints staggered between rows.  Loosely butt recover boards together[ and fasten to deck].

Retain joint taping of recover boards in subparagraph below to protect molded- or extruded-polystyrene insulation against damage from hot roofing asphalt and to minimize effect of offsets at joints between adjacent boards.

1. Tape joints of recover boards if required by membrane roofing system manufacturer.

Delete subparagraphs below if recover boards will be loosely laid, such as for ballasted roofing membranes and protected membrane roofing.  Fastening of recover boards may not be needed for new mechanically fastened roofing membranes, depending on recover board size and spacing of membrane fasteners.  Roofing membrane fasteners may be adequate to prevent shuffling or movement of recover boards under membrane during high winds.

2. Fasten to resist wind-uplift pressure at corners, perimeter, and field of roof specified in Division 07 Section "[Built-up Asphalt Roofing] <Insert Section title>."

3. Install additional fasteners near board corners and edges as necessary to conform boards to substrate and to adjacent boards.

3.10 DISPOSAL

A. Collect and place demolished materials in containers.  Promptly dispose of demolished materials.  Do not allow demolished materials to accumulate on-site.

1. Storage or sale of demolished items or materials on-site will not be permitted.

B. Transport demolished materials off Owner's property and legally dispose of them.

END OF SECTION 070150.19

	PREPARATION FOR RE-ROOFING
	070150.19 - 1



