Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
05/04 (R 05/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 071354 - THERMOPLASTIC SHEET WATERPROOFING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. PVC sheet waterproofing.

2. Molded-sheet drainage panels.

3. Insulation.

4. Plaza deck pavers[ and paver pedestals].

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 07 Section "Joint Sealants" for joint-sealant materials and installation.

1.3 SUBMITTALS

A. Product Data:  Include manufacturer's written instructions for evaluating, preparing, and treating substrate, technical data, and tested physical and performance properties of waterproofing.

B. Shop Drawings:  Show locations and extent of waterproofing.  Include details for substrate joints and cracks, sheet flashings, penetrations, inside and outside corners, tie-ins with adjoining waterproofing, and other termination conditions.

Retain subparagraph below if using pedestal-supported concrete pavers on plaza decks over waterproofing.

1. Include setting drawings showing layout, sizes, sections, profiles, and joint details of pedestal-supported concrete pavers.

C. Samples:  For the following products:

Delete Samples in subparagraphs below not required.  Add number or revise size of Samples if applicable.

1. 12-by-12-inch (300-by-300-mm) square of waterproofing.

2. 12-by-12-inch (300-by-300-mm) square of insulation.

3. 4-by-4-inch (100-by-100-mm) square of drainage panel.

4. Plaza deck paver, [4-by-4-inch (100-by-100-mm) square] [full sized], in each color and texture required.

5. Paver pedestal assembly.

Retain paragraph below if retaining "Installer Qualifications" Paragraph in "Quality Assurance" Article.

D. Installer Certificates:  Signed by manufacturers certifying that installers comply with requirements.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For Installer.

F. Product Test Reports:  Based on evaluation of comprehensive tests performed by a qualified testing agency, for waterproofing.

G. Warranties:  Special warranties specified in this Section.

1.4 QUALITY ASSURANCE

Delete paragraph below if not applicable.  For warranty purposes, a manufacturer may qualify an installer.  Coordinate options in paragraph with qualifications that manufacturer requires of Installer.  Retain first option if manufacturer approves or licenses installers.  Retain second option if placing minimal restrictions on Installer.

A. Installer Qualifications:  A firm that is [approved or licensed by] [acceptable to] waterproofing manufacturer for installation of waterproofing required for this Project.

Retain applicable products from options in paragraph below.

B. Source Limitations:  Obtain waterproofing materials[, protection course,] [board insulation,] [and] [molded-sheet drainage panels] through one source from a single manufacturer.

Delete paragraph and subparagraphs below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.  If not using pavers, delete optional sentence in paragraph and option in subparagraph below.

C. Mockups:  Before beginning installation, install waterproofing to 100 sq. ft. (9.3 sq. m) <Insert area> of [deck] [wall] to demonstrate surface preparation, crack and joint treatment, corner treatment, and execution quality.[  Install pavers and paver supports to demonstrate aesthetic affects and set quality standards for materials and execution.]

1. If Architect determines mockups do not comply with requirements, reapply waterproofing[ and reinstall overlying construction] until mockups are approved.

Retain subparagraph below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 01 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

2. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

Delete paragraph and subparagraph below if Work of this Section is not extensive or complex enough to justify a preinstallation conference.

D. Preinstallation Conference:  Conduct conference at Project site.

1. Review waterproofing requirements including surface preparation, substrate condition and pretreatment, minimum curing period, forecasted weather conditions, special details and sheet flashings, installation procedures, testing and inspection procedures, and protection and repairs.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Deliver liquid materials to Project site in original packages with seals unbroken, labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storing and mixing with other components.

B. Store liquid materials in their original undamaged packages in a clean, dry, protected location and within temperature range required by waterproofing manufacturer.

C. Remove and replace liquid materials that cannot be applied within their stated shelf life.

D. Store rolls according to manufacturer's written instructions.

E. Protect stored materials from direct sunlight.

1.6 PROJECT CONDITIONS

A. Environmental Limitations:  Apply waterproofing within the range of ambient and substrate temperatures recommended by waterproofing manufacturer.  Do not apply waterproofing to a damp or wet substrate.

1. Do not apply waterproofing in snow, rain, fog, or mist.

B. Maintain adequate ventilation during preparation and application of waterproofing materials.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."  Example in paragraph below is a labor-and-material warranty.  Manufacturers' warranties customarily do not include costs of excavating and exposing the waterproofing membrane as well as backfilling and restoring affected construction in vertical applications.

A. Special Manufacturer's Warranty:  Manufacturer's standard form in which [manufacturer agrees] [manufacturer and Installer agree] to repair or replace waterproofing that does not comply with requirements or that fails to remain watertight within specified warranty period.

Verify available warranties and insert number in subparagraph below.  Warranty periods of 5 and 10 years are available.

1. Warranty Period:  [Five] [10] <Insert number> years from date of Substantial Completion.

Retain paragraph and subparagraph below if a separate installer's warranty is required and if this is an accepted practice locally.  Usually retain special manufacturer's warranty above with special Installer's warranty below.  Coordinate requirements of both special warranties to clarify responsibilities.  If a specific installer's warranty form is required, see Division 07 low-slope roofing Sections for examples that may be modified for waterproofing.

B. Special Installer's Warranty:  Specified form, [on warranty form at end of this Section, ]signed by Installer, covering Work of this Section, for warranty period of [two] <Insert number> years.

Retain subparagraph below, revised if necessary, for plaza decks.

1. Warranty includes removing and reinstalling protection board, drainage panels, insulation, pedestals, and pavers on plaza decks.

PART 2 -  PRODUCTS

2.1 SHEET WATERPROOFING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

A. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

B. Products:  Subject to compliance with requirements, provide one of the following:

1. Sarnafil US Division, Sarnafil, Inc.; System [1000] [2000] [3000] [4001] [4002] [4003] [4004] [4005] [4006].

2. <Insert manufacturer's name; product name or designation.>

Revise thickness in paragraph below to suit Project.  Minimum sheet thickness for vertical walls is 80 mils (2.0 mm).  Distinguish thicknesses for vertical wall and plaza deck applications if applicable.

C. PVC Sheet:  [80-mil- (2.0-mm-)] [96-mil- (2.4-mm-)] [120-mil- (3.0-mm-)] thick, flexible sheet compounded from PVC resin, plasticizers, stabilizers, fillers, and pigments and reinforced with nonwoven fiberglass with the following properties measured per standard test methods referenced:

1. Tensile Strength:  1600 psi (11 MPa) minimum; ASTM D 638.

2. Elongation at Break:  250 percent minimum, machine direction; ASTM D 638.

3. Seam Strength:  90 percent minimum of tensile strength; ASTM D 638.

4. Retention of Properties after Heat Aging:  95 percent minimum retention of tensile strength and elongation; ASTM D 638 after 168 hours at 194 deg F (90 deg C); ASTM D 3045.

5. Tear Resistance:  23 lbf (102 N) minimum; ASTM D 1004.

6. Low-Temperature Bend:  Pass at minus 40 deg F (minus 40 deg C); ASTM D 2136.

7. Linear Dimension Change:  0.01 percent maximum after 6 hours at 176 deg F (80 deg C); ASTM D 1204.

8. Water Absorption:  2 percent maximum weight gain after 168 hours' immersion at 158 deg F (70 deg C); ASTM D 570.

2.2 AUXILIARY MATERIALS

A. General:  Furnish auxiliary materials recommended by waterproofing manufacturer for intended use and compatible with sheet waterproofing.

1. Furnish liquid-type auxiliary materials that comply with VOC limits of authorities having jurisdiction.

B. Concealed Sheet Flashing:  Sheet flashing of same material, construction, and thickness as sheet waterproofing.

Retain paragraph below if sheet flashings are exposed.

C. Exposed Sheet Flashing:  [60-mil- (1.5-mm-)] [80-mil- (2.0-mm-)] [96-mil- (2.4-mm-)] thick, coated PVC; reinforced with nonwoven fiberglass.

Retain first paragraph below for sheets fully adhered, partially adhered, or loosely laid with adhered containment grids.

D. Bonding Adhesives:  Adhesive for bonding polymeric sheets and sheet flashings to substrates and projections.

E. Containment Strip:  Manufacturer's standard asphalt-resistant, 60-mil- (1.5-mm-) thick, PVC strip; reinforced with nonwoven fiberglass; 12 inches (300 mm) wide.

F. Geotextile Leveling Layer:  Manufacturer's standard nonwoven polypropylene.

G. Separation Layer:  0.160-inch- (4.06-mm-) thick, nonwoven polyester felt.

H. Control Test Drain:  Manufacturer's standard four-component pipe assembly.

I. Waterproofing and Sheet Flashing Accessories:  Provide PVC discs, sealants, pourable sealers, cone and vent flashings, inside and outside corner flashings, termination reglets, clamps, compression bars, tapes, and other accessories recommended by waterproofing manufacturer for intended use.

J. Metal Termination Bars:  Manufacturer's standard stainless-steel or aluminum bars, prepunched, with nylon anchors and stainless-steel pins.

Select type of protection course from two paragraphs below if required.  First describes Sarnafil's HDPE sheet for heavy-duty protection; second describes Sarnafil's PVC sheet for regular-duty protection.  Verify acceptability of type of protection course with waterproofing manufacturer.  Distinguish locations such as plaza deck and foundation walls if both types are required.

K. Protection Course:  39-mil- (1.0-mm-) thick, hot-air-weldable, HDPE sheet protection layer.

L. Protection Course:  51-mil- (1.3-mm-) thick, hot-air-weldable, PVC sheet protection layer.

2.3 MOLDED-SHEET DRAINAGE PANELS

Retain this Article if molded-sheet drainage panels are required.  Retain paragraph below if molded-sheet drainage panel products are specified in another Section.

A. Molded-Sheet Drainage Panel:  Comply with Division 33 Section "Subdrainage."

Retain one or both paragraphs below if specifying drainage panels in this Section.  Retain first paragraph if specifying nonwoven-geotextile-faced drainage panels, usually for foundation walls.  Examples of products described below include Sarnafil's "Drainage Panel 600" and "Drainage Panel 620" with a polymeric film backing.

B. Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel:  Manufactured composite subsurface drainage panels consisting of a nonwoven, needle-punched geotextile facing with an apparent opening size not exceeding No. 70 (0.21-mm) sieve laminated to 1 side [with] [or] [without] a polymeric film bonded to the other side of a 3-dimensional, nonbiodegradable, molded-plastic-sheet drainage core, with a vertical flow rate of at least 15 gpm per ft. (188 L/min. per m).

Retain paragraph below if specifying woven-geotextile-faced drainage panels with minimal description of features.  Example of product described below includes Sarnafil's "Drainage Panel 900."

C. Woven-Geotextile-Faced, Molded-Sheet Drainage Panel:  Manufactured composite subsurface drainage panels consisting of a woven-geotextile facing with an apparent opening size not exceeding No. 40 (0.425-mm) sieve laminated to 1 side of a 3-dimensional, nonbiodegradable, molded-plastic-sheet drainage core, with a horizontal flow rate not less than 4 gpm per ft. (49 L/min. per m).

2.4 INSULATION

Retain paragraph and subparagraphs below if board insulation is required over waterproofing and if board insulation forms the first layer beneath an insulation drainage panel.

A. Board Insulation:  Extruded-polystyrene board insulation complying with ASTM C 578, [square] [or] [shiplap] edged.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Diversifoam Products.

b. Dow Chemical Company (The).

c. Owens Corning.

d. Pactiv Building Products.

e. T. Clear Corporation.

f. <Insert manufacturer's name.>

Types IV and VI insulation below are usually limited to vertical applications.  Types VII and V insulation, with higher compressive strengths, are used on plaza decks.

3. Type IV, 25-psi (173-kPa) minimum compressive strength.

4. Type VI, 40-psi (276-kPa) minimum compressive strength.

5. Type VII, 60-psi (414-kPa) minimum compressive strength.

6. Type V, 100-psi (690-kPa) minimum compressive strength.

Retain paragraph and subparagraphs below for unfaced insulation drainage panels for foundation wall applications.  Diversifoam's "CertiFoam 25 Drainage Board," Dow's "Perimate," and Pactiv's "Green-Guard-DC" are Type IV.  Diversifoam's "CertiFoam 40 Drainage Board" is Type VI.

B. Unfaced Wall Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, [Type IV, 25-psi (173-kPa)] [or] [Type VI, 40-psi (276-kPa)] minimum compressive strength; unfaced; fabricated with shiplap or channel edges and with 1 side having grooved drainage channels.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Diversifoam Products; CertiFoam [25] [40] Drainage Board.

b. Dow Chemical Company (The); Perimate.

c. Pactiv Building Products; Green-Guard-DC.

d. <Insert manufacturer's name; product name or designation.>

Retain paragraph and subparagraphs below for geotextile-faced insulation drainage panels for foundation wall applications.  Owens Corning's "Insul-Drain" is Type IV; T. Clear's "Thermadry 1250" is Type VI.

C. Geotextile-Faced Wall Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, [Type IV, 25-psi (173-kPa)] [or] [Type VI, 40-psi (276-kPa)] minimum compressive strength; fabricated with tongue-and-groove edges and with 1 side having grooved drainage channels faced with nonwoven geotextile filter fabric.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Owens Corning; Insul-Drain.

b. T. Clear Corporation; Thermadry 1250.

c. <Insert manufacturer's name; product name or designation.>

Retain paragraph and subparagraphs below for plaza deck applications if unfaced insulation drainage panels with ribbed drainage channels are required.  Retain Type VI insulation for limited, intermittent pedestrian traffic or Type VII for heavier pedestrian traffic.  Dow's "Styrofoam Ribbed Roofmate" and Owens Corning's "Foamular 404 RB" are Type VI; Diversifoam's "CertiFoam Plaza Deck" and Owens Corning's "Foamular 604 RB" are Type VII.

D. Unfaced Plaza Deck Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, [Type VI, 40-psi (276-kPa)] [Type VII, 60-psi (414-kPa)] minimum compressive strength; unfaced; fabricated with shiplapped or channel edges and with 1 side having ribbed drainage channels.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Diversifoam Products; CertiFoam Plaza Deck.

b. Dow Chemical Company (The); Styrofoam Ribbed Roofmate.

c. Owens Corning; Foamular [404 RB] [604 RB].

d. <Insert manufacturer's name; product name or designation.>

Retain paragraph below if Type VII geotextile-faced insulation is required for heavy pedestrian traffic.

E. Geotextile-Faced Plaza Deck Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, Type VII, 60-psi (414-kPa) minimum compressive strength; fabricated with tongue-and-groove edges and with 1 side having grooved drainage channels faced with manufacturer's standard, nonwoven geotextile filter fabric.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. T. Clear Corporation; Thermadry 1750.

b. <Insert manufacturer's name; product name or designation.>

2.5 PLAZA DECK PAVERS

Retain this Article if plaza deck pavers are required.  Retain one of two paragraphs below if cross-referencing paver materials from other Sections.

A. Plaza Deck Pavers:  [Brick] [Concrete] [Asphalt-block] pavers specified in Division 32 Section "Unit Paving."

B. Plaza Deck Pavers:  [Granite] [Limestone] [Marble] [Quartz-based stone] [Slate] pavers specified in Division 09 Section "Stone Flooring."

Delete both paragraphs above and retain paragraph below if plaza deck concrete pavers are required.  Verify availability of deck pavers with characteristics selected.  Below describes concrete pavers commonly used in pedestal set applications over insulation and waterproofing or for placing on a setting bed.  Limit pedestal systems to pedestrian plazas.

C. Plaza Deck Pavers:  Heavyweight, hydraulically pressed, concrete units, [square edged] [with top edges beveled 3/16 inch (5 mm)], manufactured for use as plaza deck pavers; minimum compressive strength [7500 psi (52 MPa)] [6500 psi (45 MPa)] <Insert value>, ASTM C 140; absorption not greater than 5 percent, ASTM C 140; no breakage and maximum 1 percent mass loss when tested for freeze-thaw resistance according to ASTM C 67.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Hanover Architectural Products.

b. Hastings Pavement Co., Inc.

c. Roofblok Limited.

d. Sunny Brook Pressed Concrete Co.

e. Wausau Tile, Inc.; Terra-Paving Div.

f. Westile Roofing Products.

g. <Insert manufacturer's name.>

Select one thickness and one face size from options in first two subparagraphs below.  Include special paver sizes and add descriptions of custom pavers such as stair tread and riser units, coping or curbed termination pavers, and oversize pavers.

4. Thickness:  [1-5/8 inches (41 mm)] [1-3/4 inches (45 mm)] [2 inches (51 mm)] [2-3/8 inches (60 mm)] <Insert dimension>.

5. Face Size:  [8-7/8 inches (225 mm) square] [9 inches (229 mm) square] [9 by 18 inches (229 by 457 mm)] [12 inches (305 mm) square] [12 by 24 inches (305 by 610 mm)] [18 inches (457 mm) square] [24 inches (610 mm) square] [As indicated] <Insert dimensions and shape>.

6. Color:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

Delete paragraph below if using pedestal systems for paver supports.

D. Setting Bed:  Provide [aggregate] [mortar] [bituminous] setting-bed materials specified in Division 32 Section "Unit Paving."

Delete paragraph and subparagraphs below if setting-bed systems are required.  Apart from paver producers, paver pedestal manufacturers include Envirospec and Bison ScrewJack Pedestals.

E. Paver Pedestals:  Paver manufacturer's standard SBR rubber, HDPE, or polyurethane paver support assembly, including [fixed-height] [adjustable or stackable] pedestals, shims, and spacer tabs for joint spacing of [1/8 inch (3 mm)] [3/16 inch (5 mm)] [1/8 to 3/16 inch (3 to 5 mm)].

Retain one of two subparagraphs and insert list of manufacturers and products below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. <Insert, in separate subparagraphs, manufacturer's name; product name or designation.>

Retain subparagraph below if specifying Wausau's tilting and telescoping pedestals.

3. Concrete Fill:  ACI 301, compressive strength of 5000 psi (34 MPa) at 28 days and air content of 6 percent.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements and other conditions affecting performance.

1. Do not proceed with installation until after the minimum concrete curing period recommended by waterproofing manufacturer.

2. Verify that substrate is visibly dry and free of moisture.  Test for capillary moisture by plastic sheet method according to ASTM D 4263.

3. Notify Architect in writing of anticipated problems using waterproofing over substrate.

4. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 SURFACE PREPARATION

A. Clean, prepare, and treat substrates according to manufacturer's written instructions.  Provide clean, dust-free, and dry substrates for waterproofing application.

B. Mask off adjoining surfaces not receiving waterproofing to prevent spillage and overspray affecting other construction.

C. Remove grease, oil, bitumen, form-release agents, paints, curing compounds, and other penetrating contaminants or film-forming coatings from concrete.

D. Remove fins, ridges, mortar, and other projections and fill honeycomb, aggregate pockets, holes, and other voids.

E. Prepare, fill, prime, and treat joints and cracks in substrates.  Remove dust and dirt from joints and cracks according to ASTM D 4258.

F. Prepare, treat, and seal vertical and horizontal surfaces at terminations and penetrations through waterproofing and at drains and protrusions.

3.3 FULLY ADHERED SHEET INSTALLATION

Retain this Article for fully adhered horizontal sheet installation, Sarnafil's "System 2000."

A. Install fully adhered sheets over entire area to receive waterproofing according to manufacturer's written instructions.

B. Accurately align sheets and maintain uniform side and end laps of minimum dimensions required.  Stagger end laps.

C. Apply bonding adhesive to substrate at required rate and allow to partially dry.

D. Apply bonding adhesive to sheets and firmly adhere sheets to substrate.  Do not apply bonding adhesive to splice areas of sheets.

E. Secure terminations and perimeter of deck sheet waterproofing with PVC cord and metal termination bars anchored 12 inches (300 mm) o.c.

F. Apply sheet waterproofing with side laps shingled with slope of deck where possible.

G. Spread sealant bed over deck drain flange at deck drains and securely seal sheet waterproofing in place with clamping ring.

Retain first paragraph below if tie-ins to existing waterproofing are required.

H. Install fully adhered sheets and auxiliary materials to tie into existing waterproofing.

I. Repair tears, voids, and lapped seams in waterproofing not complying with requirements.  Slit and flatten fishmouths and blisters.  Patch with sheet waterproofing extending beyond repaired areas in all directions.

3.4 LOOSELY LAID SHEET INSTALLATION

Retain this Article for loosely laid horizontal or vertical installations.

A. General:  Install loosely laid sheets over entire area to receive waterproofing according to manufacturer's written instructions.

1. Install geotextile leveling layer directly over substrates and maintain minimum side and end laps.

2. Accurately align sheets and maintain uniform side and end laps of minimum dimensions required.  Stagger end laps.

Retain first subparagraph below if tie-ins to adjoining waterproofing are required.

3. Install loosely laid sheets and auxiliary materials to tie into adjoining waterproofing.

4. Repair tears, voids, and lapped seams in waterproofing not complying with requirements.  Slit and flatten fishmouths and blisters.  Patch with sheet waterproofing extending beyond repaired areas in all directions.

Horizontal applications in paragraph and subparagraphs below apply to Sarnafil's "System 1000" or split-slab portions of Sarnafil's "System 4000" series.

B. Horizontal Applications:  Secure terminations and perimeter of [deck] [mud-slab] sheet waterproofing with PVC cord and metal termination bars anchored 12 inches (300 mm) o.c.

1. Apply sheets with side laps shingled with slope of deck where possible.

2. Spread sealant bed over deck drain flange at deck drains and securely seal sheet in place with clamping ring.

Conventional vertical applications in paragraph and subparagraphs below apply to Sarnafil's "System 4001" and to vertical wall portion of Sarnafil's "System 4002."

C. Vertical Applications:  Mechanically attach leveling layer with 4-inch- (100-mm-) minimum diameter, reinforced PVC sheet discs and fasteners at required spacings.

1. Hot-air-weld sheet waterproofing to discs.

2. Secure top termination of waterproofing [with continuous, extruded-aluminum, surface-mounted, termination reglet anchored at spacings recommended by waterproofing manufacturer] [by hot-air welding to containment strips] [according to manufacturer's written instructions].

3. Terminate waterproofing on footing as follows:

a. Scarify concrete footing under containment strips to an amplitude of 1/16 inch (1.6 mm).  Apply bonding adhesive to substrate and containment strip at required rate and allow to partially dry.  Firmly adhere containment strip to substrate.

b. Hot-air-weld sheet waterproofing to containment strips.

Blind-side vertical applications in paragraph and subparagraphs below apply to vertical wall portions of Sarnafil's "Systems 4003, 4004, 4005, and 4006."  Inaccessible blind-side locations include excavation support systems such as soldier piles with wood lagging, shotcrete or slurry walls, steel sheet piles, and augered caissons waterproofed before permanent concrete foundation wall is formed.  If waterproofing is limited to blind-side vertical walls and is drained, delete "Molded-Sheet Drainage Panel Installation" Article and retain drainage panel in second subparagraph below.

D. Blind-Side Vertical Application:  As follows:

1. Install geotextile leveling layer over substrates and maintain minimum side and end laps.  Mechanically secure to substrate with 4-inch- (100-mm-) minimum diameter, reinforced PVC sheet discs and fasteners at required spacings.

Delete subparagraph above and retain first subparagraph below if drainage panels are needed in lieu of a leveling layer.

2. Place molded-sheet drainage panels over substrate and mechanically secure to substrate with 4-inch- (100-mm-) minimum diameter, reinforced PVC sheet discs and fasteners at required spacings.

3. Hot-air-weld sheet waterproofing to discs.

4. Secure top termination of waterproofing [with continuous, extruded-aluminum, surface-mounted, termination reglet anchored at spacings recommended by waterproofing manufacturer] [by hot-air welding to containment strips] [according to manufacturer's written instructions].

3.5 COMPARTMENTED, LOOSELY LAID SHEET INSTALLATION

Retain this Article for compartmented, loosely laid horizontal sheet installations.

A. Install compartmented, loosely laid sheets over entire area to receive waterproofing according to manufacturer's written instructions.

B. Accurately align sheets and maintain uniform side and end laps of minimum dimensions required.  Stagger end laps.

C. Scarify concrete deck under containment strips to an amplitude of 1/16 inch (1.6 mm).  Apply bonding adhesive to substrate and containment strip at required rate and allow to partially dry.

Grid size in subparagraph below is typical dimension offered by Sarnafil.  Revise to suit Project.

1. Firmly adhere containment strips to substrates to form grids 25 feet (7.6 m) square.

Delete first paragraph below if control test drains are not required.

D. Drill hole in decks and install control test drain within each grid.

E. Install geotextile leveling layer directly over substrate with edges lapped and extend onto containment strips.

F. Hot-air-weld sheet waterproofing to containment strips.

G. Secure terminations and perimeter of deck sheet waterproofing with PVC cord and metal termination bars anchored 12 inches (300 mm) o.c.

H. Apply sheets with side laps shingled with slope of deck where possible.

I. Spread sealant bed over deck drain flange at deck drains and securely seal sheets in place with clamping ring.

Retain first paragraph below if tie-ins to existing waterproofing are required.

J. Install compartmented, loosely laid sheet waterproofing and auxiliary materials to tie into existing waterproofing.

K. Repair tears, voids, and lapped seams in waterproofing not complying with requirements.  Slit and flatten fishmouths and blisters.  Patch with sheet waterproofing extending beyond repaired areas in all directions.

3.6 SEAM INSTALLATION

Retain this Article for hot-air-welded, PVC sheet seams.

A. Hot-air-weld side and end laps of overlapping sheets according to manufacturer's written instructions to ensure a watertight seam installation.  Inspect outside edge of seams with pointed metal probe and ensure completed laps lay flat and are free of voids, fishmouths, or wrinkles.

3.7 SHEET FLASHING INSTALLATION

A. Install sheet flashings and preformed flashing accessories and adhere to substrates according to waterproofing manufacturer's written instructions.

B. Form wall flashings using exposed sheet flashing.

C. Extend sheet flashings over deck sheet waterproofing.  Flash penetrations and field-formed inside and outside corner accessories with sheet flashing.

1. Hot-air-weld joints with deck sheet and end laps of overlapping sheet flashings and accessories to ensure a watertight seam installation.

Delete or revise first paragraph below if architectural joint systems are used.  Coordinate with Division 07 Section "Expansion Control."

D. Terminate sheet at expansion joints and discontinuous deck-to-wall or deck-to-deck joints.  Bridge and cover joints with sheet flashing.

E. Terminate and seal top of sheet flashings[ with mechanically anchored termination bars].

3.8 PROTECTION COURSE INSTALLATION

Usually retain separation layer in first paragraph below, in addition to protection course, in vertical or horizontal applications.  Sarnafil does not require separation layer if molded-sheet or fabric-faced insulation drainage panels are applied directly over HDPE protection course.

A. Install separation layer over sheet waterproofing before placing protection course.

B. Install protection course over [sheet waterproofing] [separation layer] according to manufacturer's written instructions and before beginning subsequent construction operations.  Minimize exposure of membrane.

Retain subparagraph below if required.  Sarnafil recommends welding laps if concrete is poured against protection course.

1. Hot-air-weld joint side and end laps of protection course.

3.9 MOLDED-SHEET DRAINAGE PANEL INSTALLATION

A. Place and secure molded-sheet drainage panels, with geotextile facing away from wall or deck substrate, according to manufacturer's written instructions.  Use adhesives[ or mechanical fasteners] that do not penetrate waterproofing.  Lap edges and ends of geotextile to maintain continuity.  Protect installed panels during subsequent construction.

3.10 INSULATION INSTALLATION

A. Install [one or more layers of board insulation to achieve required thickness] [and] [insulation drainage panels] over waterproofed surfaces.  Cut and fit to within 3/4 inch (19 mm) of projections and penetrations.

Delete first paragraph below if support is not required during backfilling.

B. On vertical surfaces, place and secure insulation units according to manufacturer's written instructions.

C. On horizontal surfaces, loosely lay insulation units according to manufacturer's written instructions.  Stagger end joints and tightly abut insulation units.

3.11 PLAZA DECK PAVER INSTALLATION

Delete first paragraph below if using paver pedestal supports.

A. Setting Bed:  Install setting bed in locations and of thickness indicated to comply with requirements in Division [09 Section "Stone Flooring] [32 Section "Unit Paving]."

B. Install concrete pavers in locations indicated according to manufacturer's written instructions.

Retain two paragraphs and associated subparagraph below if setting pavers on paving pedestals.

C. Accurately install [fixed] [adjustable]-height paver pedestals and accessories in locations and to elevations required.  Adjust for final level and slope with shims.

Delete concrete fill in subparagraph below unless using Wausau's tilting and telescoping paver pedestals.

1. Fill pedestal with concrete mix, strike smooth with top of pedestal, and cure according to ACI 301.

D. Loosely lay pavers on pedestals, maintaining a uniform open joint width.  Tightly seat pavers against spacers to eliminate lateral movement or drift of paving assembly.  Align joint patterns parallel in each direction.

Revise subparagraph below to suit Project.  Consider paved area layout, paver module, and construction tolerances when imposing limits.  Verify minimum dimensions with paver manufacturer.  Minimum pedestal dimensions may also govern.  Custom-dimensioned pavers or pavers scored to repeat module may be available.

1. Lay out pavers to avoid less-than-half-width pavers at perimeter or other terminations.

Add special installation requirements here.  Examples might include tread/riser units on tabs or treatment of pavers at plaza/building expansion joints.

E. Install pavers to not vary more than 1/16 inch (1.6 mm) in elevation between adjacent pavers or more than 1/16 inch (1.6 mm) from surface plane elevation of individual paver.

F. Maintain tolerances of paving installation within [1/4 inch in 10 feet (1:48)] <Insert surface tolerance> of surface plane in any direction.

3.12 FIELD QUALITY CONTROL

Retain paragraph below if a manufacturer's site representative is required.  Manufacturer may also require this as a warranty condition.

A. Engage a full-time site representative qualified by waterproofing membrane manufacturer to inspect substrate conditions; surface preparation; membrane application, flashings, protection, and drainage components; and to furnish daily reports to Architect.

Delete flood testing when waterproofing is limited to vertical applications.  Revise first paragraph and subparagraphs below by identifying particular areas on Project to flood test when preferred.  Limit water depth to not exceed load capacity of deck.

B. Flood Testing:  Flood test each deck area for leaks, according to recommendations in ASTM D 5957, after completing waterproofing but before overlying construction is placed.  Install temporary containment assemblies, plug or dam drains, and flood with potable water.

1. Flood to an average depth of 2-1/2 inches (64 mm) with a minimum depth of 1 inch (25 mm) and not exceeding a depth of 4 inches (100 mm).  Maintain 2 inches (51 mm) of clearance from top of sheet flashings.

ASTM D 5957 sets 24 hours as minimum and 72 hours as maximum duration for flood testing.

2. Flood each area for [24] [48] [72] hours.

3. After flood testing, repair leaks, repeat flood tests, and make further repairs until waterproofing installation is watertight.

C. [Owner will engage] [Engage] an independent testing agency to observe flood testing and examine underside of decks and terminations for evidence of leaks during flood testing.

3.13 PROTECTION AND CLEANING

Retain first paragraph below for horizontal applications.

A. Do not permit foot or vehicular traffic on unprotected membrane.

B. Protect waterproofing from damage and wear during remainder of construction period.

Retain first paragraph below when board insulation or insulation drainage panels are required and may be exposed for a period on plaza decks.

C. Protect installed [board insulation] [insulation drainage panels] from damage due to UV light, harmful weather exposures, physical abuse, and other causes.  Provide temporary coverings where insulation will be subject to abuse and cannot be concealed and protected by permanent construction immediately after installation.

D. Clean spillage and soiling from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

Add Special Installer's Warranty Form here if required.

END OF SECTION 071354

	THERMOPLASTIC SHEET WATERPROOFING
	071354 - 1



