Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
08/04 (R 05/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 072726 - FLUID-APPLIED MEMBRANE AIR BARRIERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Fluid-applied membrane air barrier, vapor retarding.

2. Fluid-applied membrane air barrier, vapor permeable.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 01 Section "Allowances" for testing and inspecting allowances.

2. Division 04 Section "Unit Masonry" for embedded flashings.

3. Division 06 Section "Sheathing" for wall sheathings, wall sheathing joint-and-penetration treatments, building paper, and building wraps.

4. Division 07 low-slope roofing Sections for roof air barriers.

5. Division 07 Section "Thermal Insulation" for foam-plastic board insulation.

6. Division 07 Section "Modified Bituminous Sheet Air Barriers."

7. Division 07 Section "Sheet Metal Flashing and Trim" for sheet metal flashings.

8. Division 07 Section "Joint Sealants" for joint-sealant materials and installation.

1.3 DEFINITIONS

Retain abbreviation and term that remain after this Section has been edited.

A. ABAA:  Air Barrier Association of America.

B. Air Barrier Assembly:  The collection of air barrier materials and auxiliary materials applied to an opaque wall, including joints and junctions to abutting construction, to control air movement through the wall.

1.4 PERFORMANCE REQUIREMENTS

Retain one of first two options in paragraph below depending on whether a vapor-retarding or -permeable air barrier is required.  Consider retaining third option if air barrier will serve as a primary or secondary drainage plane.

A. General:  Air barrier shall be capable of performing as a continuous vapor-[retarding] [permeable] air barrier[ and as a liquid-water drainage plane flashed to discharge to the exterior incidental condensation or water penetration].  Air barrier assemblies shall be capable of accommodating substrate movement and of sealing substrate expansion and control joints, construction material changes, and transitions at perimeter conditions without deterioration and air leakage exceeding specified limits.

Retain paragraph below if quantitative testing in Part 1 "Preconstruction Testing" Article or in Part 3 "Field Quality Control" Article is retained.  Air leakage values below are for opaque wall assemblies, excluding windows and doors and other openings.  Although this Section is limited to one component of the assembly (the membrane air barrier), the performance of the air barrier assembly, made up of several wall components, is verifiable.

B. Air Barrier Assembly Air Leakage:  Not to exceed [0.01 cfm x sq. ft. of surface area at 1.57 lbf/sq. ft. (0.05 L/s x sq. m of surface area at 75 Pa)] [0.02 cfm x sq. ft. of surface area at 1.57 lbf/sq. ft. (0.1 L/s x sq. m of surface area at 75 Pa)] [0.03 cfm x sq. ft. of surface area at 1.57 lbf/sq. ft. (0.15 L/s x sq. m of surface area at 75 Pa)] [0.04 cfm x sq. ft. of surface area at 1.57 lbf/sq. ft. (0.2 L/s x sq. m of surface area at 75 Pa)]; [ASTM E 283] [ASTM E 783] <Insert test>.

1.5 PRECONSTRUCTION TESTING

Retain this Article if preconstruction testing of mockups is required.  Mockup testing is usually limited to buildings with complex, unusual, or previously untested exterior envelope construction. Coordinate mockup testing with mockup requirements in "Quality Assurance" Article and with Owner's testing and inspecting requirements.

A. Mockup Testing:  Air barrier assemblies shall comply with performance requirements indicated, as evidenced by reports based on mockup testing by a qualified testing agency.

1. Owner will engage a qualified testing agency.

Retain subparagraph below if nonquantitative testing is required.

2. Qualitative Testing:  Mockups will be tested for evidence of air leakage according to [ASTM E 1186, smoke pencil with pressurization or depressurization] [ASTM E 1186, chamber pressurization or depressurization with smoke tracers] [ASTM E 1186, chamber depressurization using detection liquids].

Delete subparagraph below if quantitative air leakage testing of mockup is not required.

3. Quantitative Air Leakage Testing:  Testing of the mockup for air leakage will be conducted not to exceed the test pressure differential, positive and negative, indicated in "Performance Requirements" Article for air barrier assembly air leakage when tested according to [ASTM E 283] [ASTM E 783] <Insert test>.

Retain subparagraph below if required.

4. Notify Architect [seven] <Insert number> days in advance of the dates and times when mockup testing will take place.

1.6 SUBMITTALS

A. Product Data:  Include manufacturer's written instructions for evaluating, preparing, and treating substrate; technical data; and tested physical and performance properties of air barrier.

B. Shop Drawings:  Show locations and extent of air barrier.  Include details for substrate joints and cracks, counterflashing strip, penetrations, inside and outside corners, terminations, and tie-ins with adjoining construction.

1. Include details of interfaces with other materials that form part of air barrier.

2. Include details of mockups.

C. Product Certificates:  For air barriers, certifying compatibility of air barrier and accessory materials with Project materials that connect to or that come in contact with the barrier; signed by product manufacturer.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For Applicator.

E. Product Test Reports:  Based on evaluation of comprehensive tests performed by a qualified testing agency, for air barriers.

1.7 QUALITY ASSURANCE

Delete paragraph below if not applicable.  If retaining, consider the merits and associated costs of ABAA's Quality Assurance Program before retaining option.  ABAA-licensed contractors may not be readily available; verify availability before specifying.

A. Applicator Qualifications:  A firm experienced in applying air barrier materials similar in material, design, and extent to those indicated for this Project, whose work has resulted in applications with a record of successful in-service performance [and that is an ABAA-licensed contractor, employs certified and registered installers, and complies with ABAA's Quality Assurance Program] <Insert requirements>.

Delete paragraph and subparagraphs below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.  Retain below with or without "Preconstruction Testing" Article and coordinate requirements.

B. Mockups:  Before beginning installation of air barrier, build mockups of exterior wall assembly [shown on Drawings][, 150 sq. ft. (14 sq. m)] <Insert dimensions>, incorporating backup wall construction, external cladding, window, door frame and sill, insulation, and flashing to demonstrate surface preparation, crack and joint treatment, and sealing of gaps, terminations, and penetrations of air barrier membrane.

1. Coordinate construction of mockup to permit inspection by Owner's testing agency of air barrier before external insulation and cladding is installed.

2. Include junction with roofing membrane[, building corner condition,] [and] [foundation wall intersection].

3. If Architect determines mockups do not comply with requirements, reconstruct mockups and apply air barrier until mockups are approved.

Retain subparagraph below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 01 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

4. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

Delete paragraph and subparagraphs below if Work of this Section is not extensive or complex enough to justify a preinstallation conference.

C. Preinstallation Conference:  Conduct conference at Project site.

1. Include installers of other construction connecting to air barrier, including roofing, waterproofing, architectural precast concrete, masonry, sealants, windows, glazed curtain walls, and door frames.

2. Review air barrier requirements including surface preparation, substrate condition and pretreatment, minimum substrate curing period, forecasted weather conditions, special details and sheet flashings, mockups, installation procedures, sequence of installation, testing and inspecting procedures, and protection and repairs.

1.8 DELIVERY, STORAGE, AND HANDLING

A. Store liquid materials in their original undamaged packages in a clean, dry, protected location and within temperature range required by air barrier manufacturer.

B. Remove and replace liquid materials that cannot be applied within their stated shelf life.

C. Store rolls according to manufacturer's written instructions.

D. Protect stored materials from direct sunlight.

1.9 PROJECT CONDITIONS

A. Environmental Limitations:  Apply air barrier within the range of ambient and substrate temperatures recommended by air barrier manufacturer.  Protect substrates from environmental conditions that affect performance of air barrier.  Do not apply air barrier to a damp or wet substrate or during snow, rain, fog, or mist.

PART 2 -  PRODUCTS

2.1 FLUID-APPLIED MEMBRANE AIR BARRIER

Vapor-retarding membranes function as air barriers, and vapor retarders and are usually located on the warm side of primary wall insulation.  Because the warm-side location within a wall cross section may be different in cold northern climates than in warm southern climates with air-conditioned interiors, dew point calculations or more sophisticated vapor-flow analyses may be needed to determine location of air barrier.

A. Fluid-Applied, Vapor-Retarding Membrane Air Barrier:  [Elastomeric, modified bituminous] [or] [synthetic polymer] membrane.

See Editing Instruction No. 1 in the Evaluations in Division 07 Section "Air Barriers" for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

Consult ABAA's Web site for a current listing of reviewed air barrier products.

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Elastomeric Modified Bituminous Membrane:

Review Project requirements for VOC limitations.  Henry Company's "Air-Bloc 06" is solvent type with VOC content of 370 g/L.  Remaining products are waterborne types with lower VOC contents.

1) Carlisle Coatings & Waterproofing; Barriseal.

2) Henry Company; Air-Bloc 06.

3) Meadows, W. R., Inc.; Air-Shield LM.

4) NEI; AC [AVS1] [AVS2].

5) Tremco Incorporated; ExoAir.

6) <Insert manufacturer's name; product name or designation.>

b. Synthetic Polymer Membrane:

Henry Company's "Air-Bloc 21" is trowel grade, "Air-Bloc 21S" is spray grade, and "Air-Bloc 21FR" is fire resistive, for use in fire-rated wall assemblies.  Its "Air-Bloc" 20-series products are solvent type; "Air-Bloc 32" is waterborne type.

1) Grace, W. R. & Co.; Perm-A-Barrier Liquid.

2) Henry Company; Air-Bloc [21 or 21S] [21FR] [32].

3) Rubber Polymer Corporation; Rub-R-Wall Airtight.

4) <Insert manufacturer's name; product name or designation.>

3. Physical and Performance Properties:

Air and vapor permeance in two subparagraphs below are based on energy-conservation requirements of the Massachusetts State Building Code, 780 CMR, Chapter 13.

a. Membrane Air Permeance:  Not to exceed 0.004 cfm x sq. ft. of surface area at 1.57-lbf/sq. ft. (0.02 L/s x sq. m of surface area at 75-Pa) <Insert value> pressure difference; ASTM E 2178.

b. Membrane Vapor Permeance:  Not to exceed 0.1 perm (5.8 ng/Pa x s x sq. m) <Insert value>; ASTM E 96.

Retain vapor-permeable air barrier in paragraph and subparagraphs below if air barrier is located on the cold side of primary wall insulation.  The cold-side location within a wall cross section may be different in cold northern climates than in warm southern climates with air-conditioned interiors.  A separate vapor retarder may also be required at a different location within the wall.  See the Evaluations in Division 07 Section "Air Barriers."

B. Fluid-Applied, Vapor-Permeable Membrane Air Barrier:  [Elastomeric, modified bituminous] [or] [synthetic polymer] membrane.

See Editing Instruction No. 1 in the Evaluations in Division 07 Section "Air Barriers" for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers and products below.  See Division 01 Section "Product Requirements."

Consult ABAA's Web site for a current listing of reviewed air barrier products.

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Elastomeric, Modified Bituminous Membrane:

Henry Company's "Air-Bloc 07" is solvent type with a perm rating of 4 and a VOC content not greater than 350 g/L.

1) Henry Company; Air-Bloc 07.

2) <Insert manufacturer's name; product name or designation.>

b. Synthetic Polymer Membrane:

Both products in first subparagraph below are polymer emulsions with perm ratings exceeding 10 and VOC contents of 100 g/L.  Henry Company's "Air-Bloc 33" has enhanced UV resistance.

1) Henry Company; Air-Bloc [31] [33].

2) <Insert manufacturer's name; product name or designation.>

3. Physical and Performance Properties:

Air permeance in first subparagraph below is based on energy-conservation requirements of the Massachusetts State Building Code, 780 CMR, Chapter 13.  Revise to suit Project.

a. Membrane Air Permeance:  Not to exceed [0.004 cfm/ sq. ft. of surface area at 1.57-lbf/sq. ft. (0.02 L/s x sq. m of surface area at 75-Pa)] <Insert value> pressure difference; ASTM E 2178.

b. Membrane Vapor Permeance:  Not less than [10 perms (580 ng/Pa x s x sq. m)] [4 perms (243 ng/Pa x s x sq. m)] <Insert value>; ASTM E 96.

2.2 AUXILIARY MATERIALS

A. General:  Auxiliary materials recommended by air barrier manufacturer for intended use and compatible with air barrier membrane.  Liquid-type auxiliary materials shall comply with VOC limits of authorities having jurisdiction.

Both types of liquid primer in paragraph below may be used on concrete, masonry, gypsum and wood-based sheathings, metal, and painted substrates.

B. Primer:  Liquid [waterborne] [solvent-borne] primer recommended for substrate by manufacturer of air barrier material.

Modified bituminous self-adhering strip in paragraph below is used to counterflash metal flashings.

C. Counterflashing Strip:  Modified bituminous, 40-mil- (1.0-mm-) thick, self-adhering sheet consisting of 32 mils (0.8 mm) of rubberized asphalt laminated to an 8-mil- (0.2-mm-) thick, crosslaminated polyethylene film with release liner backing.

Butyl-based self-adhering strip in first paragraph below is used to terminate air barrier to EPDM or TPO roofing membranes.

D. Butyl Strip:  Vapor-retarding, 30- to 40-mil- (0.76- to 1.0-mm-) thick, self-adhering; polyethylene-film-reinforced top surface laminated to layer of butyl adhesive with release liner backing.

Modified bituminous self-adhering strip in first paragraph below is used to terminate air barrier to compatible roofing membranes.  Verify compatibility with roofing membranes and revise strip material if necessary.

E. Modified Bituminous Strip:  Vapor-retarding, 40-mil- (1.0-mm-) thick, smooth-surfaced, self-adhering; consisting of 36 mils (0.9 mm) of rubberized asphalt laminated to a 4-mil- (0.1-mm-) thick polyethylene film with release liner backing.

F. Joint Reinforcing Strip:  Air barrier manufacturer's glass-fiber-mesh tape.

G. Substrate Patching Membrane:  Manufacturer's standard trowel-grade substrate filler.

H. Adhesive and Tape:  Air barrier manufacturer's standard adhesive and pressure-sensitive adhesive tape.

I. Stainless-Steel Sheet:  ASTM A 240/A 240M, Type 304, [0.0187 inch (0.5 mm)] [0.0250 inch (0.64 mm)] <Insert dimension> thick, and Series 300 stainless-steel fasteners.

Foam sealant in paragraph below is used to fill gaps at penetrations and openings.

J. Sprayed Polyurethane Foam Sealant:  1- or 2-component, foamed-in-place, polyurethane foam sealant, 1.5 to 2.0 lb/cu. ft (24 to 32 kg/cu. m) density; flame spread index of 25 or less according to ASTM E 162; with primer and noncorrosive substrate cleaner recommended by foam sealant manufacturer.

Retain one or more of first four paragraphs below for materials to seal air barrier terminations with windows, doors, curtain walls, and storefront systems.  Retain first paragraph if using a vapor-retarding, modified bituminous transition strip.  Retain second paragraph if using a vapor-permeable, adhesive-coated transition strip.  Retain third paragraph if using an elastomeric flashing sheet.  Retain fourth paragraph if using a preformed silicone-sealant extrusion.

K. Modified Bituminous Transition Strip:  Vapor-retarding, 40-mil- (1.0-mm-) thick, smooth-surfaced, self-adhering; consisting of 36 mils (0.9 mm) of rubberized asphalt laminated to a 4-mil- (0.1-mm-) thick polyethylene film with release liner backing.

Vapor-permeable strip in first paragraph below describes Henry Company's "Blueskin Breather" that may be used instead of a vapor-retarding, modified bituminous transition strip; usually with a fluid-applied, vapor-permeable membrane air barrier.

L. Adhesive-Coated Transition Strip:  Vapor-permeable, 17-mil- (0.43-mm-) thick, self-adhering strip consisting of an adhesive coating over a permeable laminate with a permeance of 37 perms (2145 ng/Pa x s x sq. m).

M. Elastomeric Flashing Sheet:  ASTM D 2000, 2BC415 to 3BC620, minimum 50- to 65-mil- (1.3- to 1.6-mm-) thick, cured sheet neoprene with manufacturer's recommended contact adhesives and lap sealant with [stainless-steel termination bars and fasteners] [aluminum termination bars and stainless-steel fasteners] [galvanized steel termination bars and fasteners].

Products described in paragraph below include Dow Corning Corporation's "123 Silicone Seal," GE Silicones' "UltraSpan US1100," Pecora Corporation's "Sil-Span," and Tremco Incorporated's "Spectrem EZ Seal."

N. Preformed Silicone-Sealant Extrusion:  Manufacturer's standard system consisting of cured low-modulus silicone extrusion, sized to fit opening widths, with a single-component, neutral-curing, Class 100/50 (low-modulus) silicone sealant for bonding extrusions to substrates.

Revise paragraph below to specify another compatible joint sealant if required.  Polysulfide or polyurethane joint sealants may be incompatible with bituminous sheet materials or with bituminous-based materials on adjoining surfaces.

O. Joint Sealant:  ASTM C 920, single-component, neutral-curing silicone; Class 100/50 (low-modulus), Grade NS, Use NT related to exposure, and, as applicable to joint substrates indicated, Use O.  Comply with Division 07 Section "Joint Sealants."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements and other conditions affecting performance.

1. Verify that substrates are sound and free of oil, grease, dirt, excess mortar, or other contaminants.

2. Verify that concrete has cured and aged for minimum time period recommended by air barrier manufacturer.

3. Verify that concrete is visibly dry and free of moisture.  Test for capillary moisture by plastic sheet method according to ASTM D 4263.

4. Verify that masonry joints are flush and completely filled with mortar.

5. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 SURFACE PREPARATION

A. Clean, prepare, treat, and seal substrate according to manufacturer's written instructions.  Provide clean, dust-free, and dry substrate for air barrier application.

B. Mask off adjoining surfaces not covered by air barrier to prevent spillage and overspray affecting other construction.

C. Remove grease, oil, bitumen, form-release agents, paints, curing compounds, and other penetrating contaminants or film-forming coatings from concrete.

D. Remove fins, ridges, mortar, and other projections and fill honeycomb, aggregate pockets, holes, and other voids in concrete with substrate patching membrane.

E. Remove excess mortar from masonry ties, shelf angles, and other obstructions.

F. At changes in substrate plane, apply sealant or termination mastic beads at sharp corners and edges to form a smooth transition from one plane to another.

G. Cover gaps in substrate plane and form a smooth transition from one substrate plane to another with stainless-steel sheet mechanically fastened to structural framing to provide continuous support for air barrier.

3.3 JOINT TREATMENT

A. Concrete and Masonry:  Prepare, treat, rout, and fill joints and cracks in substrate according to ASTM C 1193 and air barrier manufacturer's written instructions.  Remove dust and dirt from joints and cracks complying with ASTM D 4258 before coating surfaces.

1. Prime substrate and apply a single thickness of preparation coat strip extending a minimum of 3 inches (75 mm) along each side of joints and cracks.  Apply a double thickness of air barrier membrane and embed a joint reinforcing strip in preparation coat.

B. Gypsum Sheathing:  Fill joints greater than 1/4 inch (6 mm) with sealant according to ASTM C 1193 and with air barrier manufacturer's written instructions.  Apply first layer of fluid air barrier membrane at joints.  Tape joints with joint reinforcing strip after first layer is dry.  Apply a second layer of fluid air barrier membrane over joint reinforcing strip.

3.4 TRANSITION STRIP INSTALLATION

Revise this Article to coordinate with drawing details.  Sheet or liquid seal materials should be placed over a firm backing to provide structural support for achieving an effective and permanent air barrier.

A. Install strips, transition strips, and auxiliary materials according to air barrier manufacturer's written instructions to form a seal with adjacent construction and maintain a continuous air barrier.

1. Coordinate the installation of air barrier with installation of roofing membrane and base flashing to ensure continuity of air barrier with roofing membrane.

2. Install [butyl] [modified bituminous] strip on roofing membrane or base flashing so that a minimum of 3 inches (75 mm) of coverage is achieved over both substrates.

B. Apply primer to substrates at required rate and allow to dry.  Limit priming to areas that will be covered by air barrier sheet in same day.  Reprime areas exposed for more than 24 hours.

Delete subparagraph below if glass-fiber-surfaced gypsum sheathing is not used.

1. Prime glass-fiber-surfaced gypsum sheathing with number of prime coats needed to achieve required bond, with adequate drying time between coats.

C. Connect and seal exterior wall air barrier membrane continuously to roofing membrane air barrier, concrete below-grade structures, floor-to floor construction, exterior glazing and window systems, glazed curtain-wall systems, storefront systems, exterior louvers, exterior door framing, and other construction used in exterior wall openings, using accessory materials [as indicated].

D. At end of each working day, seal top edge of strips and transition strips to substrate with termination mastic.

E. Apply joint sealants forming part of air barrier assembly within manufacturer's recommended application temperature ranges.  Consult manufacturer when sealant cannot be applied within these temperature ranges.

F. Wall Openings:  Prime concealed perimeter frame surfaces of windows, curtain walls, storefronts, and doors.  Apply [modified bituminous transition strip] [adhesive-coated transition strip] [elastomeric flashing sheet] [preformed silicone-sealant extrusion] so that a minimum of 3 inches (75 mm) of coverage is achieved over both substrates.  Maintain 3 inches (75 mm) of full contact over firm bearing to perimeter frames with not less than 1 inch (25 mm) of full contact.

Retain one of three subparagraphs below, depending on option selected in paragraph above.

1. [Modified Bituminous] [Adhesive-Coated] Transition Strip:  Roll firmly to enhance adhesion.

2. Elastomeric Flashing Sheet:  Apply adhesive to wall, frame, and flashing sheet.  Install flashing sheet and termination bars, fastened at 6 inches (150 mm) o.c.  Apply lap sealant over exposed edges and on cavity side of flashing sheet.

3. Preformed Silicone-Sealant Extrusion:  Set in full bed of silicone sealant applied to walls, frame, and membrane.

G. Fill gaps in perimeter frame surfaces of windows, curtain walls, storefronts, and doors, and miscellaneous penetrations of air barrier membrane with foam sealant.

Retain paragraph below if strips and transition strips will follow installation of projecting interior wythe masonry ties or joint reinforcement.

H. Seal strips and transition strips around masonry reinforcing or ties and penetrations with termination mastic.

Retain first option in first paragraph below if flashings are nonmetallic; retain second option for metal through-wall flashings.

I. Seal top of through-wall flashings to air barrier with an additional 6-inch- (150-mm-) wide, [modified bituminous] [counterflashing] strip.

J. Seal exposed edges of strips at seams, cuts, penetrations, and terminations not concealed by metal counterflashings or ending in reglets with termination mastic.

K. Repair punctures, voids, and deficient lapped seams in strips and transition strips.  Slit and flatten fishmouths and blisters.  Patch with transition strips extending 6 inches (150 mm) beyond repaired areas in strip direction.

3.5 AIR BARRIER MEMBRANE INSTALLATION

A. Apply air barrier membrane to form a seal with strips and transition strips and to achieve a continuous air barrier according to air barrier manufacturer's written instructions.

B. Apply air barrier membrane within manufacturer's recommended application temperature ranges.

Retain one or both paragraphs and subparagraphs below if priming of substrates is required; verify requirements with manufacturer.

C. Apply primer to substrates at required rate and allow to dry.  Limit priming to areas that will be covered by air barrier sheet in same day.  Reprime areas exposed for more than 24 hours.

Delete subparagraph below if glass-fiber-surfaced gypsum sheathing is not used.

1. Prime glass-fiber-surfaced gypsum sheathing with number of prime coats needed to achieve required bond, with adequate drying time between coats.

D. Apply a continuous unbroken air barrier to substrates according to the following minimum thickness.  Apply membrane in full contact around protrusions such as masonry ties.

Retain one of two subparagraphs below.  Verify minimum thickness recommended by manufacturers; recommended thickness may vary with substrate.

1. Vapor-Retarding Membrane Air Barrier:  [60-mil (1.5-mm)] [40-mil (1.0-mm)] [120-mil (3.0-mm)] <Insert dimension> dry film thickness.

2. Vapor-Permeable Membrane Air Barrier:  [120-mil (3.0-mm) wet film thickness] [215-mil (5.5-mm) wet film thickness] [47-mil (1.2-mm) minimum dry film thickness] <Insert dimension>.

Retain one or both options in first paragraph below.  Most manufacturers overlap membrane to previously placed strip and transition strip; W. R. Grace applies strip and transition strip over cured membrane.  Verify manufacturer's current recommendations.

E. Apply [strip and transition strip a minimum of 1 inch (25 mm) onto cured air membrane] [or] [strip and transition strip over cured air membrane overlapping 3 inches (75 mm) onto each surface] according to air barrier manufacturer's written instructions.

F. Do not cover air barrier until it has been tested and inspected by Owner's testing agency.

G. Correct deficiencies in or remove air barrier that does not comply with requirements; repair substrates and reapply air barrier components.

3.6 FIELD QUALITY CONTROL

Coordinate test and inspection requirements in this Article with input from Owner's testing agency.

A. Testing Agency:  Owner will engage a qualified testing agency to perform tests and inspections and prepare test reports.

B. Inspections:  Air barrier materials and installation are subject to inspection for compliance with requirements.  Inspections may include the following:

Retain list of inspections below if required for Contractor's information.

1. Continuity of air barrier system has been achieved throughout the building envelope with no gaps or holes.

2. Continuous structural support of air barrier system has been provided.

3. Masonry and concrete surfaces are smooth, clean and free of cavities, protrusions, and mortar droppings.

4. Site conditions for application temperature and dryness of substrates have been maintained.

5. Maximum exposure time of materials to UV deterioration has not been exceeded.

6. Surfaces have been primed, if applicable.

7. Laps in strips and transition strips have complied with minimum requirements and have been shingled in the correct direction (or mastic has been applied on exposed edges), with no fishmouths.

8. Termination mastic has been applied on cut edges.

9. Strips and transition strips have been firmly adhered to substrate.

10. Compatible materials have been used.

11. Transitions at changes in direction and structural support at gaps have been provided.

12. Connections between assemblies (membrane and sealants) have complied with requirements for cleanliness, preparation and priming of surfaces, structural support, integrity, and continuity of seal.

13. All penetrations have been sealed.

C. Tests:  Testing to be performed will be determined by Owner's testing agency from among the following tests:

Retain subparagraph below if nonquantitative testing is required.

1. Qualitative Testing: Air barrier assemblies will be tested for evidence of air leakage according to [ASTM E 1186, smoke pencil with pressurization or depressurization] [ASTM E 1186, chamber pressurization or depressurization with smoke tracers] [ASTM E 1186, chamber depressurization using detection liquids].

Other quantitative tests may include ASTM E 779; CAN/CGSB 149.10, "Determination of the Airtightness of Building Envelopes by the Fan Depressurization Method"; and CAN/CGSB 149.15, "Determination of the Overall Envelope Airtightness of Office Buildings by the Fan Depressurization Method Using the Building's Air Handling System."  Insert other testing requirements below if applicable.

Delete subparagraph below if quantitative air leakage testing of mockup is not required.

2. Quantitative Air Leakage Testing:  Testing not to exceed the test pressure differential, positive and negative, indicated in "Performance Requirements" Article for air barrier assembly air leakage according to [ASTM E 283] [ASTM E 783] [ASTM E 1677] <Insert test>.

D. Remove and replace deficient air barrier components and retest as specified above.

3.7 CLEANING AND PROTECTION

A. Protect air barrier system from damage during application and remainder of construction period, according to manufacturer's written instructions.

1. Protect air barrier from exposure to UV light and harmful weather exposure as required by manufacturer.  Remove and replace air barrier exposed for more than [30] [60] <Insert number> days.

2. Protect air barrier from contact with creosote, uncured coal-tar products, TPO, EPDM, flexible PVC membranes, and sealants not approved by air barrier manufacturer.

B. Clean spills, stains, and soiling from construction that would be exposed in the completed work using cleaning agents and procedures recommended by manufacturer of affected construction.

C. Remove masking materials after installation.

END OF SECTION 072726

	FLUID-APPLIED MEMBRANE AIR BARRIERS
	072726 - 1



