Copyright 2005 AIA
MASTERSPEC Full Length
08/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 089000 - LOUVERS AND VENTS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Fixed, [extruded-aluminum] [and] [formed-metal] louvers.

2. Adjustable, [extruded-aluminum] [and] [formed-metal] louvers.

3. Adjustable, [extruded-aluminum] [and] [formed-metal] insulated louvers.

4. Fixed, formed-metal acoustical louvers.

5. Wall vents (brick vents).

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 04 Section "Unit Masonry" for building wall vents (brick vents) into masonry.

2. Division 08 Section "Hollow Metal Doors and Frames" for louvers in hollow-metal doors.

3. Division 08 Section "Flush Wood Doors" for louvers in flush wood doors.

4. Division 09 Section "Exterior Painting" for field painting louvers.

5. Division 22 Section "General-Service Compressed-Air Piping" for connecting pneumatic-operated adjustable louvers.

6. Division 23 Sections for louvers that are a part of mechanical equipment.

7. Division 23 Section "Instrumentation and Control for HVAC" for electric, electronic, and pneumatic control of adjustable louvers.

8. Division 26 Sections for electrical power connections for motor-operated adjustable louvers.

1.3 DEFINITIONS

Retain definitions remaining after this Section has been edited.

A. Louver Terminology:  Definitions of terms for metal louvers contained in AMCA 501 apply to this Section unless otherwise defined in this Section or in referenced standards.

B. Horizontal Louver:  Louver with horizontal blades; i.e., the axes of the blades are horizontal.

C. Vertical Louver:  Louver with vertical blades; i.e., the axes of the blades are vertical.

D. Drainable-Blade Louver:  Louver with blades having gutters that collect water and drain it to channels in jambs and mullions, which carry it to bottom of unit and away from opening.

E. Storm-Resistant Louver:  Louver that provides specified wind-driven rain performance, as determined by testing according to AMCA 500-L.

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.  Most louver manufacturers will not have an engineer on staff who is legally authorized to practice in the jurisdiction where Project is located.  For this reason, it is advisable to delete below unless large louvers are used.  If specifying large or structurally complex louvers and relying on manufacturer for information about their structural performance, below can be retained and louver manufacturer or Contractor can engage a local engineer to prepare the required calculations.

A. Delegated Design:  Design louvers, including comprehensive engineering analysis by a qualified professional engineer, using structural[ and seismic] performance requirements and design criteria indicated.

B. Structural Performance:  Louvers shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated without permanent deformation of louver components, noise or metal fatigue caused by louver blade rattle or flutter, or permanent damage to fasteners and anchors.  Wind pressures shall be considered to act normal to the face of the building.

Retain one of first three subparagraphs below.  If retaining first, indicate pressures on appropriate elevation Drawings.  Requirements in second and third subparagraphs are examples only.  Revise to suit Project.  Consult a structural engineer to quantify design loads applicable to Project.  Verify compliance with codes.  See Evaluations.

1. Wind Loads:  Determine loads based on pressures as indicated on Drawings.

2. Wind Loads:  Determine loads based on a uniform pressure of [20 lbf/sq. ft. (957 Pa)] [30 lbf/sq. ft. (1436 Pa)] <Insert design wind pressure>, acting inward or outward.

3. Wind Loads:  Determine loads based on pressures indicated below:

a. Corner Zone:  Within <Insert distance> of building corners, uniform pressure of <Insert design wind pressure>, acting inward, and <Insert design wind pressure>, acting outward.

b. Other Than Corner Zone:  Uniform pressure of <Insert design wind pressure>, acting inward, and <Insert design wind pressure>, acting outward.

Revise first paragraph below to indicate specific loads determined by Project's structural engineer or refer to loads indicated on Drawings.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

C. Seismic Performance:  Louvers, including attachments to other construction, shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Design earthquake spectral response acceleration, short period (Sds) is determined by Project's location and site classification.  This information is usually provided in structural notes on Drawings.

1. Design earthquake spectral response acceleration, short period (Sds) for Project is <Insert value>.

Component Importance Factor is generally 1.0 unless the structure is in Seismic Use Group III and louver is necessary for continued operation of facility or failure of louver could impair continued operation of facility, in which case it is 1.5.

2. Component Importance Factor is [1.5] [1.0].

First paragraph below may not be needed for most louvers, but should be retained if continuous louver assemblies are used.

D. Thermal Movements:  Allow for thermal movements from ambient and surface temperature changes, without buckling, opening of joints, overstressing of components, failure of connections, or other detrimental effects.

Differential values in subparagraph below (for aluminum in particular) are suitable for most of the U.S.

1. Temperature Change (Range):  [120 deg F (67 deg C), ambient; 180 deg F (100 deg C)] <Insert temperature range>, material surfaces.

Delete first paragraph below and performance ratings in Part 2 if louvers are sufficiently oversized that performance is not critical.

E. Louver Performance Ratings:  Provide louvers complying with requirements specified, as demonstrated by testing manufacturer's stock units identical to those provided, except for length and width according to AMCA 500-L.

Delete paragraph below if no acoustical louvers.

F. Acoustic Performance:  Provide acoustical louvers complying with ratings specified, as demonstrated by testing manufacturer's stock units identical to those specified, except for length and width for [airborne sound-transmission loss according to ASTM E 90] [outdoor-indoor sound-transmission loss according to ASTM E 966].

1.5 SUBMITTALS

First four paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.

1. For louvers specified to bear AMCA seal, include printed catalog pages showing specified models with appropriate AMCA Certified Ratings Seals.

B. Shop Drawings:  For louvers and accessories.  Include plans, elevations, sections, details, and attachments to other work.  Show frame profiles and blade profiles, angles, and spacing.

1. Show weep paths, gaskets, flashing, sealant, and other means of preventing water intrusion.

2. Show mullion profiles and locations.

3. Wiring Diagrams:  For power, signal, and control wiring for motorized adjustable louvers.

C. Samples for Initial Selection:  For units with factory-applied color finishes.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph below with or without above.

D. Samples for Verification:  For each type of metal finish required.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

E. Delegated-Design Submittal:  For louvers indicated to comply with structural[ and seismic] performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Remaining paragraph is defined in Division 01 Section "Submittal Procedures" as an "Informational Submittal."  Reports are generally not necessary if product data bearing AMCA Certified Ratings Seal are required.

F. Product Test Reports:  Based on evaluation of comprehensive tests performed according to AMCA 500-L by a qualified testing agency or by manufacturer and witnessed by a qualified testing agency, for each type of louver and showing compliance with performance requirements specified.

1.6 QUALITY ASSURANCE

A. Source Limitations:  Obtain louvers and vents from single source from a single manufacturer where indicated to be of same type, design, or factory-applied color finish.

Delete first paragraph below if no welding is required or if weld strength is not critical.

B. Welding:  Qualify procedures and personnel according to the following:

1. AWS D1.2/D1.2M, "Structural Welding Code - Aluminum."

2. AWS D1.3, "Structural Welding Code - Sheet Steel."

3. AWS D1.6, "Structural Welding Code - Stainless Steel."

C. SMACNA Standard:  Comply with recommendations in SMACNA's "Architectural Sheet Metal Manual" for fabrication, construction details, and installation procedures.

Delete paragraph below if no motor-operated louvers.

D. UL and NEMA Compliance:  Provide motors and related components for motor-operated louvers that are listed and labeled by UL and comply with applicable NEMA standards.

1.7 PROJECT CONDITIONS

A. Field Measurements:  Verify actual dimensions of openings by field measurements before fabrication.

PART 2 -  PRODUCTS

2.1 MATERIALS

A. Aluminum Extrusions:  ASTM B 221 (ASTM B 221M), Alloy 6063-T5, T-52, or T6.

B. Aluminum Sheet:  ASTM B 209 (ASTM B 209M), Alloy 3003 or 5005 with temper as required for forming, or as otherwise recommended by metal producer for required finish.

C. Aluminum Castings:  ASTM B 26/B 26M, Alloy 319.

D. Galvanized-Steel Sheet:  ASTM A 653/A 653M, [G60 (Z180)] [G90 (Z275)] zinc coating, mill phosphatized.

E. Stainless-Steel Sheet:  ASTM A 240/A 240M, Type 304, [No. 2B finish] [No. 2D finish] [No. 4 finish, with grain running parallel to length of blades and frame members] [No. 4 finish, with grain running perpendicular to length of blades and frame members] [No. 4 finish, with grain running perpendicular to length of blades and parallel to length of frame members] [No. 6 finish].

F. Fasteners:  Use types and sizes to suit unit installation conditions.

First option in first subparagraph below specifies flush heads; second specifies raised heads.

1. Use [Phillips flat-head] [hex-head or Phillips pan-head] [tamper-resistant] screws for exposed fasteners unless otherwise indicated.

2. For fastening aluminum, use aluminum or 300 series stainless-steel fasteners.

3. For fastening galvanized steel, use hot-dip-galvanized steel or 300 series stainless-steel fasteners.

4. For fastening stainless steel, use 300 series stainless-steel fasteners.

5. For color-finished louvers, use fasteners with heads that match color of louvers.

G. Postinstalled Fasteners for Concrete and Masonry:  Torque-controlled expansion anchors, made from stainless-steel components, with capability to sustain, without failure, a load equal to 4 times the loads imposed, for concrete, or 6 times the load imposed, for masonry, as determined by testing per ASTM E 488, conducted by a qualified independent testing agency.

H. Bituminous Paint:  Cold-applied asphalt emulsion complying with ASTM D 1187.

2.2 FABRICATION, GENERAL

A. Assemble louvers in factory to minimize field splicing and assembly.  Disassemble units as necessary for shipping and handling limitations.  Clearly mark units for reassembly and coordinated installation.

B. Vertical Assemblies:  Where height of louver units exceeds fabrication and handling limitations, fabricate units to permit field-bolted assembly with close-fitting joints in jambs and mullions, reinforced with splice plates.

1. Continuous Vertical Assemblies:  Fabricate units without interrupting blade-spacing pattern [unless horizontal mullions are indicated] [where indicated].

Usually retain subparagraph above or below.  If both conditions are required, retain one subparagraph as default requirement and indicate exceptions on Drawings.

2. Horizontal Mullions:  Provide horizontal mullions at joints [unless continuous vertical assemblies are indicated] [where indicated].

Retain option in first paragraph below only if appearance of spacing at head and sill is critical; option is not possible with some designs.

C. Maintain equal louver blade spacing[, including separation between blades and frames at head and sill,] to produce uniform appearance.

D. Fabricate frames, including integral sills, to fit in openings of sizes indicated, with allowances made for fabrication and installation tolerances, adjoining material tolerances, and perimeter sealant joints.

Retain one of three options in subparagraph below as default and indicate other frame types required, if any, on Drawings.

1. Frame Type:  [Channel] [Exterior flange] [Interior flange] unless otherwise indicated.

E. Include supports, anchorages, and accessories required for complete assembly.

Coordinate first paragraph below with Drawings and product descriptions.

F. Provide vertical mullions of type and at spacings indicated, but not more than recommended by manufacturer, or 72 inches (1830 mm) o.c., whichever is less.

1. Fully Recessed Mullions:  Where indicated, provide mullions fully recessed behind louver blades.  Where length of louver exceeds fabrication and handling limitations, fabricate with close-fitting blade splices designed to permit expansion and contraction.

Retain subparagraph above or first subparagraph below if any louvers require a continuous appearance.  Note that fully recessed mullions are not available for drainable-blade louvers and that only a few manufacturers offer drainable-blade louvers with semirecessed mullions.

2. Semirecessed Mullions:  Where indicated, provide mullions partly recessed behind louver blades so louver blades appear continuous.  Where length of louver exceeds fabrication and handling limitations, fabricate with interlocking split mullions and close-fitting blade splices designed to permit expansion and contraction.

3. Exposed Mullions:  Where indicated, provide units with exposed mullions of same width and depth as louver frame.  Where length of louver exceeds fabrication and handling limitations, provide interlocking split mullions designed to permit expansion and contraction.

Delete subparagraph below if no exterior mitered corners.  If retaining, verify available corner construction with manufacturers selected.

4. Exterior Corners:  Prefabricated corner units with mitered [and welded blades] [blades with concealed close-fitting splices] and with [fully recessed] [semirecessed] mullions at corners.

Subsills and extended sills should be shown on Drawings.

G. Provide [subsills made of same material as louvers] [or] [extended sills] for recessed louvers.

H. Join frame members to each other and to fixed louver blades with fillet [welds concealed from view] [welds, threaded fasteners, or both, as standard with louver manufacturer] unless otherwise indicated or size of louver assembly makes bolted connections between frame members necessary.

2.3 FIXED, EXTRUDED-ALUMINUM LOUVERS

A. Horizontal Storm-Resistant Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Construction Specialties, Inc.

h. Greenheck Fan Corporation.

i. Industrial Louvers, Inc.

j. NCA Manufacturing, Inc.

k. Nystrom Building Products.

l. Reliable Products, Inc.

m. Ruskin Company; Tomkins PLC.

n. United Enertech Corp.

o. <Insert manufacturer's name>.

Requirements in first two subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [4 inches (100 mm)] [5 inches (125 mm)] [7 inches (175 mm)] [8 inches (200 mm)] [9 inches (225 mm)] <Insert depth>.

Usually retain second option in first subparagraph below; blades of storm-resistant louvers gain stiffness from their complex shapes and, therefore, do not need to be as thick as blades of some other louver types.  If retaining first option, verify availability of louvers with performance requirements selected.

4. Frame and Blade Nominal Thickness:  Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Louver Performance Ratings:

Requirements for free area and air performance in first two subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [5.0 sq. ft. (0.46 sq. m)] [6.0 sq. ft. (0.56 sq. m)] [7.0 sq. ft. (0.65 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

c. Wind-Driven Rain Performance:  Not less than [99] [95] [80] <Insert rating> percent effectiveness when subjected to a rainfall rate of [3 inches (75 mm) per hour and a wind speed of 29 mph (13 m/s)] [8 inches (200 mm) per hour and a wind speed of 50 mph (22.4 m/s)] at a core-area intake velocity of [300 fpm (1.5 m/s)] [400 fpm (2.0 m/s)] [500 fpm (2.5 m/s)] <Insert velocity>.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

6. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

B. Vertical Storm-Resistant Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Cesco Products; a division of Mestek, Inc.

h. Construction Specialties, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Louvers & Dampers, Inc.; a division of Mestek, Inc.

l. NCA Manufacturing, Inc.

m. Nystrom Building Products.

n. Reliable Products, Inc.

o. Ruskin Company; Tomkins PLC.

p. United Enertech Corp.

q. <Insert manufacturer's name>.

Requirements in first two subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] [8 inches (200 mm)] [9 inches (225 mm)] [12 inches (300 mm)] <Insert depth>.

Usually retain second option in first subparagraph below; blades of storm-resistant louvers gain stiffness from their complex shapes and, therefore, do not need to be as thick as blades of some other louver types.  If retaining first option, verify availability of louvers with performance requirements selected.

4. Frame and Blade Nominal Thickness:  Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Louver Performance Ratings:

Requirements for free area and air performance in first two subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice may limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [5.0 sq. ft. (0.46 sq. m)] [6.0 sq. ft. (0.56 sq. m)] [7.0 sq. ft. (0.65 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

Most vertical storm-resistant louvers will provide 99 percent effectiveness under the most severe conditions.

c. Wind-Driven Rain Performance:  Not less than 99 percent effectiveness when subjected to a rainfall rate of [3 inches (75 mm) per hour and a wind speed of 29 mph (13 m/s)] [8 inches (200 mm) per hour and a wind speed of 50 mph (22.4 m/s)] at a core-area intake velocity of [300 fpm (1.5 m/s)] [400 fpm (2.0 m/s)] [500 fpm (2.5 m/s)] <Insert velocity>.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

6. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

C. Horizontal, Drainable-Blade Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Carnes Company, Inc.

h. Cesco Products; a division of Mestek, Inc.

i. Construction Specialties, Inc.

j. Dowco Products Group; Safe-Air of Illinois, Inc.

k. Greenheck Fan Corporation.

l. Industrial Louvers, Inc.

m. Louvers & Dampers, Inc.; a division of Mestek, Inc.

n. Metal Form Manufacturing Inc.

o. NCA Manufacturing, Inc.

p. Nystrom Building Products.

q. Reliable Products, Inc.

r. Ruskin Company; Tomkins PLC.

s. United Enertech Corp.

t. Vent Products Company, Inc.

u. <Insert manufacturer's name>.

Requirements in first two subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required.  If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

4. Frame and Blade Nominal Thickness:  Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Mullion Type:  Exposed.

6. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first four subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] [8.5 sq. ft. (0.79 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

In first subparagraph below, usually retain 900 to 1050 fpm (4.6 to 5.3 m/s) for 4-inch (100-mm) louvers and 950 to 1100 fpm (4.8 to 5.6 m/s) for 6-inch (150-mm) louvers.

b. Point of Beginning Water Penetration:  Not less than [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] [1000 fpm (5.1 m/s)] [1050 fpm (5.3 m/s)] [1100 fpm (5.6 m/s)] <Insert velocity>.

Retain one of first two subparagraphs below.  If retaining first subparagraph, usually retain 700 to 800 fpm (3.6 to 4.1 m/s) for 4-inch (100-mm) louvers and 750 to 850 fpm (3.8 to 4.3 m/s) for 6-inch (150-mm) louvers.  Do not specify free-area velocity in either subparagraph that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] [800-fpm (4.1-m/s)] [850-fpm (4.3-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

d. Air Performance:  Not more than [0.15-inch wg (37-Pa)] <Insert pressure> static pressure drop at [900-fpm (4.6-m/s)] [950-fpm (4.8-m/s)] [1000-fpm (5.1-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

7. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

D. Horizontal, Continuous-Line, Drainable-Blade Louver <Insert drawing designation, e.g., LV-1>:  Drainable-blade louver with blade gutters (drains) in rear two-thirds of blades only and with semirecessed mullions capable of collecting and draining water from blades.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Airolite Company, LLC (The).

b. Arrow United Industries; a division of Mestek, Inc.

c. Construction Specialties, Inc.

d. Greenheck Fan Corporation.

e. Ruskin Company; Tomkins PLC.

f. <Insert manufacturer's name>.

Requirements in first two subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [6 inches (150 mm)] <Insert depth>.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required.  If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

4. Frame and Blade Nominal Thickness:  Not less than 0.080 inch (2.03 mm).

5. Louver Performance Ratings:

a. Free Area:  Not less than [7.8 sq. ft. (0.72 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than [850 fpm (4.3 m/s)] <Insert velocity>.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [800-fpm (4.1-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

E. Horizontal, Sightproof, Drainable-Blade Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Construction Specialties, Inc.

h. Dowco Products Group; Safe-Air of Illinois, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Louvers & Dampers, Inc.; a division of Mestek, Inc.

l. NCA Manufacturing, Inc.

m. Nystrom Building Products.

n. Reliable Products, Inc.

o. Ruskin Company; Tomkins PLC.

p. United Enertech Corp.

q. <Insert manufacturer's name>.

Requirements in first two subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [5 inches (125 mm)] <Insert depth>.

Usually retain second option in first subparagraph below; blades of sightproof louvers gain stiffness from their complex shapes and, therefore, do not need to be as thick as blades of some other louver types.  If retaining first option, verify availability of louvers with performance requirements selected.

4. Frame and Blade Nominal Thickness:  Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Mullion Type:  Exposed.

6. Louver Performance Ratings:

a. Free Area:  Not less than [8.3 sq. ft. (0.77 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than [750 fpm (3.8 m/s)] [950 fpm (4.8 m/s)] <Insert velocity>.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [550-fpm (2.8-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

F. Horizontal, Nondrainable-Blade Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Carnes Company, Inc.

h. Cesco Products; a division of Mestek, Inc.

i. Construction Specialties, Inc.

j. Dowco Products Group; Safe-Air of Illinois, Inc.

k. Greenheck Fan Corporation.

l. Louvers & Dampers, Inc.; a division of Mestek, Inc.

m. Metal Form Manufacturing Inc.

n. NCA Manufacturing, Inc.

o. Nystrom Building Products.

p. Reliable Products, Inc.

q. Ruskin Company; Tomkins PLC.

r. United Enertech Corp.

s. Vent Products Company, Inc.

t. <Insert manufacturer's name>.

Requirements in first three subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [2 inches (50 mm)] [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>.

4. Blade Profile:  [Plain blade without] [Blade with] center baffle.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required.  If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

5. Frame and Blade Nominal Thickness:  Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

6. Mullion Type:  [Exposed] [Semirecessed] [Fully recessed].

7. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in three subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] [8.5 sq. ft. (0.79 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than [700 fpm (3.6 m/s)] [750 fpm (3.8 m/s)] [800 fpm (4.1 m/s)] [850 fpm (4.3 m/s)] [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] <Insert velocity>.

Do not specify free-area velocity in subparagraph below that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [650-fpm (3.3-m/s)] [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

Paragraph below is a descriptive specification for use where factors affecting appearance are critical.  If vertical louvers are required and louver performance is critical, copy performance requirements above for horizontal louvers and revise values to match those in manufacturers' catalogs for vertical louvers.

G. Vertical, Sightproof, Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. American Warming and Ventilating, Inc.; a Mestek company.

e. Arrow United Industries; a division of Mestek, Inc.

f. Cesco Products; a division of Mestek, Inc.

g. Construction Specialties, Inc.

h. Dowco Products Group; Safe-Air of Illinois, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Ruskin Company; Tomkins PLC.

l. United Enertech Corp.

m. <Insert manufacturer's name>.

Requirements in first two subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [4 inches (100 mm)] <Insert depth>.

4. Blade Profile:  [Chevron] [Y] [Labyrinth]-shaped blade.

Usually retain second option in first subparagraph below; blades of sightproof louvers gain stiffness from their complex shapes and, therefore, do not need to be as thick as blades of some other louver types.

5. Frame and Blade Nominal Thickness:  Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

6. Blade Spacing:  [2 inches (50 mm)] [4 inches (100 mm)] <Insert spacing> o.c.

7. Mullion Type:  [Exposed] [Semirecessed] [Fully recessed].

2.4 FIXED, FORMED-METAL LOUVERS

A. Horizontal, Drainable-Blade Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. American Warming and Ventilating, Inc.; a Mestek company.

e. Arrow United Industries; a division of Mestek, Inc.

f. Cesco Products; a division of Mestek, Inc.

g. Construction Specialties, Inc.

h. Dowco Products Group; Safe-Air of Illinois, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Metal Form Manufacturing Inc.

l. NCA Manufacturing, Inc.

m. Ruskin Company; Tomkins PLC.

n. United Enertech Corp.

o. Vent Products Company, Inc.

p. <Insert manufacturer's name>.

Requirements in first three subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required.  If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

4. Frame and Blade Material and Nominal Thickness:  Galvanized-steel sheet, not less than [0.052 inch (1.32 mm) for frames and 0.040 inch (1.02 mm) for blades] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

5. Frame and Blade Material and Nominal Thickness:  Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

6. Mullion Type:  Exposed.

7. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first four subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] [8.5 sq. ft. (0.79 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than [800 fpm (4.1 m/s)] [850 fpm (4.3 m/s)] [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] [1000 fpm (5.1 m/s)] <Insert velocity>.

Retain one of first two subparagraphs below.  Do not specify free-area velocity in either subparagraph that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] [800-fpm (4.1-m/s)] [850-fpm (4.3-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

d. Air Performance:  Not more than [0.15-inch wg (37-Pa)] <Insert pressure> static pressure drop at [900-fpm (4.6-m/s)] [950-fpm (4.8-m/s)] [1000-fpm (5.1-m/s)] <Insert velocity> free-area velocity.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

8. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

B. Horizontal, Nondrainable-Blade Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. American Warming and Ventilating, Inc.; a Mestek company.

e. Arrow United Industries; a division of Mestek, Inc.

f. Cesco Products; a division of Mestek, Inc.

g. Construction Specialties, Inc.

h. Dowco Products Group; Safe-Air of Illinois, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Metal Form Manufacturing Inc.

l. NCA Manufacturing, Inc.

m. Ruskin Company; Tomkins PLC.

n. United Enertech Corp.

o. Vent Products Company, Inc.

p. <Insert manufacturer's name>.

Requirements in first four subparagraphs below are based on products available from listed manufacturers.  Revise to suit Project.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>.

4. Blade Profile:  [Plain blade without] [Blade with] center baffle.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required.  If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

5. Frame and Blade Material and Nominal Thickness:  Galvanized-steel sheet, not less than [0.052 inch (1.32 mm) for frames and 0.040 inch (1.02 mm) for blades] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

6. Frame and Blade Material and Nominal Thickness:  Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

7. Mullion Type:  [Exposed] [Semirecessed] [Fully recessed].

8. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in three subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [6.5 sq. ft. (0.60 sq. m)] [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than [550 fpm (2.8 m/s)] [600 fpm (3.0 m/s)] [650 fpm (3.3 m/s)] [700 fpm (3.6 m/s)] <Insert velocity>.

Do not specify free-area velocity in subparagraph below that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [550-fpm (2.8-m/s)] [600-fpm (3.0-m/s)] [650-fpm (3.3-m/s)] [700-fpm (3.6-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

2.5 ADJUSTABLE, EXTRUDED-ALUMINUM LOUVERS

A. Louver Construction and Operation:  Provide adjustable louvers with extruded-aluminum frames and blades not less than 0.080-inch (2.03-mm) nominal thickness, and with operating mechanisms to suit louver sizes.

Retain one operation method in five subparagraphs below; delete others.  Revise to suit specific requirements.

1. Hand operation with push bars.

2. Crank operation with removable-crank operator in sill or jamb.

3. Chain operation with tension spring, wall clip, pull chain, and 160 deg F (71 deg C) fusible link.

Options in first subparagraph below are examples of available motor operators and control features.

4. Motor operation with [2-position, spring-return application (with power on, motor opens louver; with power off, spring closes louver); 110-V, 60-Hz motor and limit switch] [2-direction, 110-V, 60-Hz motor and limit switches]; equipped with [frame-mounted switch] [remote-mounted switch with indicator light] [terminals for controlling devices].

Subparagraph below is an example of pneumatic operators available from one louver manufacturer.

5. Pneumatic piston operation for use with 80- to 100-psi (550- to 690-kPa) compressed air for [2-position] [modulating] operation; power open, power close[ with spring-return fail-safe].

B. Dual-Blade, Drainable-Blade, Adjustable Louver <Insert drawing designation, e.g., LV-1>:  Fixed drainable blades and adjustable plain blades combined in single frame.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Carnes Company, Inc.

h. Cesco Products; a division of Mestek, Inc.

i. Construction Specialties, Inc.

j. Dowco Products Group; Safe-Air of Illinois, Inc.

k. Greenheck Fan Corporation.

l. Industrial Louvers, Inc.

m. Louvers & Dampers, Inc.; a division of Mestek, Inc.

n. NCA Manufacturing, Inc.

o. Metal Form Manufacturing Inc.

p. Reliable Products, Inc.

q. Ruskin Company; Tomkins PLC.

r. United Enertech Corp.

s. Vent Products Company, Inc.

t. <Insert manufacturer's name>.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>, overall.

4. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first three subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [6.0 sq. ft. (0.56 sq. m)] [6.5 sq. ft. (0.60 sq. m)] [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than [750 fpm (3.8 m/s)] [800 fpm (4.1 m/s)] [850 fpm (4.3 m/s)] [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] [1000 fpm (5.1 m/s)] <Insert velocity>.

Do not specify free-area velocity in first subparagraph below that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [750-fpm (3.8-m/s)] [800-fpm (4.1-m/s)] [850-fpm (4.3-m/s)] [900-fpm (4.6-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

d. Air Leakage:  Not more than [1.5 cfm/sq. ft. (7.6 L/s per sq. m)] <Insert air-leakage rating> of louver gross area at a differential static pressure of 0.15-inch wg (37 Pa) with adjustable louver blades closed.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

5. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

C. Single-Blade, Adjustable Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Carnes Company, Inc.

h. Cesco Products; a division of Mestek, Inc.

i. Construction Specialties, Inc.

j. Dowco Products Group; Safe-Air of Illinois, Inc.

k. Greenheck Fan Corporation.

l. Industrial Louvers, Inc.

m. Louvers & Dampers, Inc.; a division of Mestek, Inc.

n. Metal Form Manufacturing Inc.

o. NCA Manufacturing, Inc.

p. Reliable Products, Inc.

q. Ruskin Company; Tomkins PLC.

r. United Enertech Corp.

s. Vent Products Company, Inc.

t. <Insert manufacturer's name>.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>.

4. Blade Type:  [Drainable] [Plain].

5. Accessories:  Equip louvers as follows:

a. Vinyl blade-edge gaskets for each louver blade.

Retain first subparagraph below (not recommended by Airolite, with removable crank or concealed motor operator) only after verifying suitability with type of actuator specified.  Revise to suit products of manufacturers selected.

b. [Stainless-steel jamb seals] [or] [vinyl blade-end gaskets].

6. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first three subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [6.5 sq. ft. (0.60 sq. m)] [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

Coordinate options in first subparagraph below with blade type selected; for plain-blade adjustable louvers, point of beginning water penetration ranges from 500 to 800 fpm (2.5 to 4.1 m/s); for drainable-blade adjustable louvers, from 600 to 1250 fpm (3.0 to 6.4 m/s).

b. Point of Beginning Water Penetration:  Not less than [500 fpm (2.5 m/s)] [600 fpm (3.0 m/s)] [700 fpm (3.6 m/s)] [800 fpm (4.1 m/s)] [900 fpm (4.6 m/s)] [1000 fpm (5.1 m/s)] <Insert velocity>.

Do not specify free-area velocity in first subparagraph below that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [500-fpm (2.5-m/s)] [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] [900-fpm (4.6-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

Only a few manufacturers offer AMCA performance-rated adjustable louvers.  If nonrated units are acceptable, delete first subparagraph below.

d. Air Leakage:  Not more than [3.5 cfm/sq. ft. (17.8 L/s per sq. m)] <Insert air-leakage rating> of louver gross area at a differential static pressure of 0.15-inch wg (37 Pa) with adjustable louver blades closed.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

7. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

2.6 ADJUSTABLE, FORMED-METAL LOUVERS

A. Louver Operation:  Provide adjustable louvers with operating mechanisms to suit louver sizes.

Retain one operation method in five subparagraphs below; delete others.  Revise to suit specific requirements.

1. Hand operation with push bars.

2. Crank operation with removable-crank operator in sill or jamb.

3. Chain operation with tension spring, wall clip, pull chain, and 160 deg F (71 deg C) fusible link.

Options in first subparagraph below are examples of available motor operators and control features.

4. Motor operation with [2-position, spring-return application (with power on, motor opens louver; with power off, spring closes louver); 110-V, 60-Hz motor and limit switch] [2-direction, 110-V, 60-Hz motor and limit switches]; equipped with [frame-mounted switch] [remote-mounted switch with indicator light] [terminals for controlling devices].

Subparagraph below is an example of pneumatic operators available from one louver manufacturer.

5. Pneumatic piston operation for use with 80- to 100-psi (550- to 690-kPa) compressed air for [2-position] [modulating] operation; power open, power close[ with spring-return fail-safe].

B. Dual-Blade, Drainable-Blade, Adjustable Louver <Insert drawing designation, e.g., LV-1>:  Fixed drainable blades and adjustable plain blades combined in single frame.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Dowco Products Group; Safe-Air of Illinois, Inc.

b. Metal Form Manufacturing Inc.

c. Ruskin Company; Tomkins PLC.

d. <Insert manufacturer's name>.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>, overall.

4. Frame and Blade Material and Nominal Thickness:  Galvanized-steel sheet, not less than [0.052 inch (1.32 mm) for frames and 0.040 inch (1.02 mm) for blades] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

5. Frame and Blade Material and Nominal Thickness:  Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

6. Louver Performance Ratings:

a. Free Area:  Not less than <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration:  Not less than <Insert velocity>.

Do not specify free-area velocity in first subparagraph below that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than <Insert pressure> static pressure drop at <Insert velocity> free-area [exhaust] [intake] velocity.

d. Air Leakage:  Not more than [1.5 cfm/sq. ft. (7.6 L/s per sq. m)] <Insert air-leakage rating> of louver gross area at a differential static pressure of 0.15-inch wg (37 Pa) with adjustable louver blades closed.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

7. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

C. Single-Blade, Adjustable Louver <Insert drawing designation, e.g., LV-1>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. American Warming and Ventilating, Inc.; a Mestek company.

e. Arrow United Industries; a division of Mestek, Inc.

f. Carnes Company, Inc.

g. Cesco Products; a division of Mestek, Inc.

h. Dowco Products Group; Safe-Air of Illinois, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Louvers & Dampers, Inc.; a division of Mestek, Inc.

l. Metal Form Manufacturing Inc.

m. NCA Manufacturing, Inc.

n. Ruskin Company; Tomkins PLC.

o. United Enertech Corp.

p. Vent Products Company, Inc.

q. <Insert manufacturer's name>.

3. Louver Depth:  [4 inches (100 mm)] [6 inches (150 mm)] <Insert depth>.

4. Blade Type:  [Drainable] [Plain].

5. Frame and Blade Material and Nominal Thickness:  Galvanized-steel sheet, not less than [0.052 inch (1.32 mm) for frames and 0.040 inch (1.02 mm) for blades] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

6. Frame and Blade Material and Nominal Thickness:  Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

7. Accessories:  Equip louvers as follows:

a. Vinyl blade-edge gaskets for each louver blade.

Retain first subparagraph below (not recommended by Airolite, with removable crank or concealed motor operator) only after verifying suitability with type of actuator specified.  Revise to suit products of manufacturers selected.

b. [Stainless-steel jamb seals] [or] [vinyl blade-end gaskets].

8. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first three subparagraphs below are based on products available from listed manufacturers.  If more than one choice is given for a requirement, the most lenient choice will allow many of the products in the category to comply, resulting in competitive pricing; the most restrictive choice will limit products to high-performance designs, potentially with higher costs.

a. Free Area:  Not less than [6.5 sq. ft. (0.60 sq. m)] [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] <Insert free area> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

Coordinate options in first subparagraph below with blade type selected; for plain-blade adjustable louvers, point of beginning water penetration ranges from 500 to 800 fpm (2.5 to 4.1 m/s); for drainable-blade adjustable louvers, from 600 to 1250 fpm (3.0 to 6.4 m/s).

b. Point of Beginning Water Penetration:  Not less than [500 fpm (2.5 m/s)] [600 fpm (3.0 m/s)] [700 fpm (3.6 m/s)] [800 fpm (4.1 m/s)] [900 fpm (4.6 m/s)] [1000 fpm (5.1 m/s)] <Insert velocity>.

Do not specify free-area velocity in first subparagraph below that is greater than point of beginning water penetration specified in last subparagraph above.

c. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [500-fpm (2.5-m/s)] [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] [900-fpm (4.6-m/s)] <Insert velocity> free-area [exhaust] [intake] velocity.

Only a few manufacturers offer AMCA performance-rated adjustable louvers.  If nonrated units are acceptable, delete first subparagraph below.

d. Air Leakage:  Not more than [3.5 cfm/sq. ft. (17.8 L/s per sq. m)] <Insert air-leakage rating> of louver gross area at a differential static pressure of 0.15-inch wg (37 Pa) with adjustable louver blades closed.

Verify availability of seal in subparagraph below for louver sizes indicated.  Delete if not required.  Coordinate with product data submittal requirement.

9. AMCA Seal:  Mark units with AMCA Certified Ratings Seal.

2.7 ADJUSTABLE, INSULATED LOUVERS

A. Louver Operation:  Provide adjustable louvers with operating mechanisms to suit louver sizes.

Retain one operation method in five subparagraphs below; delete others.  Revise to suit specific requirements.

1. Hand operation with push bars.

2. Crank operation with removable-crank operator in sill or jamb.

3. Chain operation with tension spring, wall clip, pull chain, and 160 deg F (71 deg C) fusible link.

Options in first subparagraph below are examples of available motor operators and control features.

4. Motor operation with [2-position, spring-return application (with power on, motor opens louver; with power off, spring closes louver); 110-V, 60-Hz motor and limit switch] [2-direction, 110-V, 60-Hz motor and limit switches]; equipped with [frame-mounted switch] [remote-mounted switch with indicator light] [terminals for controlling devices].

Subparagraph below is an example of pneumatic operators available from one louver manufacturer.

5. Pneumatic piston operation for use with 80- to 100-psi (550- to 690-kPa) compressed air for [2-position] [modulating] operation; power open, power close[ with spring-return fail-safe].

B. Adjustable, Insulated, Extruded-Aluminum Louver <Insert drawing designation, e.g., LV-1>:  Single-blade, adjustable louver with gasketed, insulated blades.  Frames and blade frames have urethane thermal break.  Frames are extruded aluminum, not less than 0.080-inch (2.03-mm) nominal thickness.  Blade facings are aluminum sheet, not less than 0.032-inch (0.81-mm) nominal thickness.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Airolite Company, LLC (The).

b. Construction Specialties, Inc.

c. <Insert manufacturer's name>.

3. Louver Depth:  [6 inches (150 mm)] [9 inches (225 mm)]

4. Insulation:  [Extruded-polystyrene foam, 2 inches (50 mm) thick] [Foamed-in-place polyurethane].

Insert performance requirements, if required, after verifying with manufacturers.

C. Adjustable, Insulated, Formed-Metal Louver <Insert drawing designation, e.g., LV-1>:  Single-blade, adjustable louver with gasketed, insulated blades.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Arrow United Industries; a division of Mestek, Inc.

b. Carnes Company, Inc.

c. Dowco Products Group; Safe-Air of Illinois, Inc.

d. Vent Products Company, Inc.

e. <Insert manufacturer's name>.

3. Louver Depth:  [6 inches (150 mm)] [8 inches (200 mm)] <Insert depth>.

4. Frame Material and Nominal Thickness:  Galvanized-steel sheet, not less than [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

5. Frame Material and Nominal Thickness:  Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

6. Blade Material and Nominal Thickness:  Galvanized-steel sheet, not less than [0.028 inch (0.71 mm)] [0.040 inch (1.02 mm)] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

7. Blade Material and Nominal Thickness:  Stainless-steel sheet, not less than [0.025 inch (0.64 mm)] [0.038 inch (0.95 mm)] [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

Louver manufacturers do not all provide the same insulation.  Deleting subparagraph below will allow maximum competition.

8. Insulation:  [Extruded-polystyrene foam, 1 inch (25 mm) thick] [Rigid, glass-fiber-board insulation, 1 inch (25 mm) thick] [Foamed-in-place polyurethane, 1/2 inch (13 mm) thick] <Insert insulation description and thickness>.

Insert performance requirements, if required, after verifying with manufacturers.

2.8 FIXED, ACOUSTICAL LOUVERS

A. Fixed, Formed-Metal Acoustical Louver <Insert drawing designation, e.g., LV-1>:  Louver with formed-metal blades filled on interior with mineral-fiber, rigid-board, acoustical insulation retained by perforated metal sheet of same material and finish as blade.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating, Inc.; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Construction Specialties, Inc.

h. Dowco Products Group; Safe-Air of Illinois, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Louvers & Dampers, Inc.; a division of Mestek, Inc.

l. Metal Form Manufacturing Inc.

m. NCA Manufacturing, Inc.

n. Reliable Products, Inc.

o. Ruskin Company; Tomkins PLC.

p. United Enertech Corp.

q. <Insert manufacturer's name>.

3. Louver Depth:  [6 inches (150 mm)] [8 inches (200 mm)] [12 inches (300 mm)] <Insert depth>.

4. Frame Material:  Extruded-aluminum or aluminum sheet, not less than 0.080-inch (2.03-mm) nominal thickness.

5. Frame Material:  Galvanized-steel sheet, not less than [0.052-inch (1.32-mm)] [0.064-inch (1.63-mm)] nominal thickness.

6. Blade Material:  Aluminum sheet, not less than [0.063-inch (1.60-mm)] [0.080-inch (2.03-mm)] nominal thickness.

7. Blade Material:  Galvanized-steel sheet, not less than [0.034-inch (0.86-mm)] [0.040-inch (1.02-mm)] [0.052-inch (1.32-mm)] nominal thickness.

8. Blade Shape:  [Straight] [Airfoil] [Chevron].

9. Blade Angle:  45 degrees unless otherwise indicated.

10. Blade Spacing:  6 inches (150 mm) o.c. for 6-inch- (150-mm-) deep louvers.

11. Blade Spacing:  [6 inches (150 mm)] [8 inches (200 mm)] o.c. for 8-inch- (200-mm-) deep louvers.

12. Blade Spacing:  [9 inches (225 mm)] [12 inches (300 mm)] o.c. for 12-inch- (300-mm-) deep louvers.

Three subparagraphs below are examples only; revise to suit Project.

13. Free Area:  Not less than 4 sq. ft. (0.37 sq. m) for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

14. Airborne Sound-Transmission Loss:  STC [10] <Insert value> per ASTM E 413, determined by testing per ASTM E 90.

15. Outdoor-Indoor Sound-Transmission Loss:  OITC [10] <Insert value> per ASTM E 1332, determined by testing per ASTM E 966.

2.9 LOUVER SCREENS

Retain one of two options in first paragraph below.  If retaining second option, indicate locations on Drawings.

A. General:  Provide screen at [each exterior louver] [louvers indicated].

Retain applicable requirements in three subparagraphs below to suit louver locations, types, and functions.  See Evaluations.

1. Screen Location for Fixed Louvers:  Interior face.

2. Screen Location for Adjustable Louvers:  [Interior] [Exterior] face unless otherwise indicated.

Retain one of three options in subparagraph below.  See Evaluations.

3. Screening Type:  [Bird screening] [Bird screening except where insect screening is indicated] [Insect screening].

B. Secure screen frames to louver frames with [stainless-steel machine screws] [machine screws with heads finished to match louver], spaced a maximum of 6 inches (150 mm) from each corner and at 12 inches (300 mm) o.c.

C. Louver Screen Frames:  Fabricate with mitered corners to louver sizes indicated.

1. Metal:  Same kind and form of metal as indicated for louver to which screens are attached.[ Reinforce extruded-aluminum screen frames at corners with clips.]

2. Finish:  [Same finish as louver frames to which louver screens are attached] [Mill finish unless otherwise indicated].

Retain one of two options in subparagraph below.  First allows screen mesh to be replaced without replacing frame, which is desirable for insect screen.  Second requires frame to be replaced when replacing screen mesh, which is typical for bird screen.

3. Type:  [Rewirable frames with a driven spline or insert] [Non-rewirable, U-shaped frames].

If more than one screen type is required, coordinate selection with Drawings and with mechanical engineer for required percentage of open area.  Retain three paragraphs below for louver material selected.  Delete all if manufacturer's standard screening is acceptable.

D. Louver Screening for Aluminum Louvers:

Retain one or more of five subparagraphs below, or insert another mesh or wire size.  If both bird screening and insect screening are required, indicate location of each on Drawings.

1. Bird Screening:  Aluminum, 1/2-inch- (13-mm-) square mesh, 0.063-inch (1.60-mm) wire.

2. Bird Screening:  Stainless steel, 1/2-inch- (13-mm-) square mesh, 0.047-inch (1.19-mm) wire.

3. Bird Screening:  Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick.

4. Insect Screening:  Aluminum, 18-by-16 (1.4-by-1.6-mm) mesh, 0.012-inch (0.30-mm) wire.

5. Insect Screening:  Stainless steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm) wire.

Delete first paragraph below if no galvanized-steel louvers.

E. Louver Screening for Galvanized-Steel Louvers:

Retain one or more of four subparagraphs below, or insert another mesh or wire size.  If both bird screening and insect screening are required, indicate location of each on Drawings.

1. Bird Screening:  Galvanized steel, 1/2-inch- (13-mm-) square mesh, 0.041-inch (1.04-mm) wire.

2. Bird Screening:  Stainless steel, 1/2-inch- (13-mm-) square mesh, 0.047-inch (1.19-mm) wire.

3. Insect Screening:  Galvanized steel, 18-by-14 (1.4-by-1.8-mm) mesh, 0.011-inch (0.28-mm) wire.

4. Insect Screening:  Stainless steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm) wire.

Delete paragraph below if no stainless-steel louvers.

F. Louver Screening for Stainless-Steel Louvers:

Retain one or both subparagraphs below, or insert another mesh or wire size.  If both bird screening and insect screening are required, indicate location of each on Drawings.

1. Bird Screening:  Stainless steel, 1/2-inch- (13-mm-) square mesh, 0.047-inch (1.19-mm) wire.

2. Insect Screening:  Stainless steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm) wire.

Insert other screening materials as required, including bronze and glass fiber.

2.10 BLANK-OFF PANELS

A. Uninsulated, Blank-Off Panels:  Metal sheet attached to back of louver.

Retain applicable metal and thickness requirements in five subparagraphs below.  Thicknesses indicated are examples only; revise to suit louver conditions.

1. Aluminum sheet for aluminum louvers, not less than 0.050-inch (1.27-mm) nominal thickness.

2. Galvanized-steel sheet for galvanized-steel louvers, not less than [0.040-inch (1.02-mm)] [0.052-inch (1.32-mm)] nominal thickness.

3. Stainless-steel sheet for stainless-steel louvers, not less than [0.038-inch (0.95-mm)] [0.050-inch (1.27-mm)] nominal thickness, with grain running in same direction as grain of louver blades.

4. Panel Finish:  [Same finish applied to louvers] [Same type of finish applied to louvers, but black color].

Retain one of two options in subparagraph below or revise to suit Project.  Other methods include slide bolts and cam latches with or without hinges.  Delete subparagraph if not important.

5. Attach blank-off panels with [clips] [sheet metal screws] <Insert method>.

B. Insulated, Blank-Off Panels:  Laminated panels consisting of insulating core surfaced on back and front with metal sheets and attached to back of louver.

1. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)].

2. Metal Facing Sheets:  Aluminum sheet, not less than 0.032-inch (0.81-mm) nominal thickness.

3. Metal Facing Sheets:  Galvanized-steel sheet, not less than 0.028-inch (0.71-mm) nominal thickness.

4. Metal Facing Sheets:  Stainless-steel sheet, not less than 0.031-inch (0.79-mm) nominal thickness.

5. Insulating Core:  [Rigid, glass-fiber-board insulation] [or] [extruded-polystyrene foam] <Insert insulation material>.

First subparagraph below is an example only; revise to suit Project.

6. Edge Treatment:  Trim perimeter edges of blank-off panels with louver manufacturer's standard [extruded-aluminum-channel frames, not less than 0.080-inch (2.03-mm) nominal thickness] [channel frames], with corners mitered and with same finish as panels.

7. Seal perimeter joints between panel faces and louver frames with gaskets or sealant.

8. Panel Finish:  [Same finish applied to louvers] [Same type of finish applied to louvers, but black color].

Retain one of two options in subparagraph below or revise to suit Project.  Other methods include slide bolts and cam latches with or without hinges.  Delete subparagraph if not important.

9. Attach blank-off panels with [clips] [sheet metal screws] <Insert method>.

2.11 WALL VENTS (BRICK VENTS)

A. Extruded-Aluminum Wall Vents:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Air Flow Company, Inc.

b. Airolite Company, LLC (The).

c. Arrow United Industries; a division of Mestek, Inc.

d. Construction Specialties, Inc.

e. Dowco Products Group; Safe-Air of Illinois, Inc.

f. Greenheck Fan Corporation.

g. Hohmann & Barnard, Inc.

h. Industrial Louvers, Inc.

i. Louvers & Dampers, Inc.; a division of Mestek, Inc.

j. Metal Form Manufacturing Inc.

k. Nystrom Building Products.

l. Reliable Products, Inc.

m. Ruskin Company; Tomkins PLC.

n. Sunvent Industries; Division of Sylro Sales Corp.

o. United Enertech Corp.

p. <Insert manufacturer's name>.

2. Extruded-aluminum louvers and frames, not less than 0.125-inch (3.18-mm) nominal thickness, assembled by welding; with 18-by-14- (1.4-by-1.8-mm-) mesh, aluminum insect screening on inside face; incorporating weep holes, continuous drip at sill, and integral waterstop on inside edge of sill; of load-bearing design and construction.

3. Dampers:  Aluminum blades and frames mounted on inside of wall vents; operated from exterior with Allen wrench in socket-head cap screw.  Fabricate operating mechanism from Type 304 stainless-steel components.

4. Finish:  [Mill finish] <Insert finish>.

B. Cast-Aluminum Wall Vents:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Airolite Company, LLC (The).

b. Greenheck Fan Corporation.

c. Hohmann & Barnard, Inc.

d. Ruskin Company; Tomkins PLC.

e. Sunvent Industries; Division of Sylro Sales Corp.

f. <Insert manufacturer's name>.

2. One-piece, cast-aluminum louvers and frames; with 18-by-14- (1.4-by-1.8-mm-) mesh, aluminum insect screening on inside face; incorporating integral waterstop on inside edge of sill; of load-bearing design and construction.

3. Dampers:  Aluminum blades and frames mounted on inside of wall vents; operated from exterior with Allen wrench in socket-head cap screw.  Fabricate operating mechanism from Type 304 stainless-steel components.

4. Finish:  Mill finish.

2.12 FINISHES, GENERAL

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

2.13 ALUMINUM FINISHES

Many louvers are made from prefinished extrusions or coil-coated metal sheet and are touched up after assembly.  Before retaining first paragraph below, verify availability and possibly cost with manufacturers selected.

A. Finish louvers after assembly.

Retain finishes in paragraphs below to suit Project.  If retaining more than one, indicate location of each on Drawings or by inserts.

Retain one of two options in first paragraph below.  Class II finish is standard with many manufacturers; Class I finish is heavy anodized.  Verify availability with manufacturers selected.

B. Clear Anodic Finish:  AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in first paragraph below.  Verify availability with manufacturers selected.

C. Color Anodic Finish:  AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

1. Color:  [Champagne] [Light bronze] [Medium bronze] [Dark bronze] [Black] <Insert color>.

Options in subparagraph above are examples only and may vary in color range and availability among manufacturers.  Retain one or delete all and retain one of two options in subparagraph below.

2. Color:  [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities].

D. Conversion-Coated Finish:  AA-C12C42 (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  acid-chromate-fluoride-phosphate conversion coating).

Delete paragraph above and retain first paragraph below if extended delay in field painting is anticipated.

E. Conversion-Coated and Factory-Primed Finish:  AA-C12C42R1x (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  acid-chromate-fluoride-phosphate conversion coating; Organic Coating:  as specified below).

Revise subparagraph below if different primer is required.

1. Organic Coating:  Air-dried primer of not less than 2-mil (0.05-mm) dry film thickness.

First paragraph below references AAMA standard for pigmented organic coating on extrusions and panels.

F. Baked-Enamel or Powder-Coat Finish:  AAMA 2603 except with a minimum dry film thickness of 1.5 mils (0.04 mm).  Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

Retain one of two paragraphs below; if both are required, indicate location of each system on Drawings, in schedules, or by inserts.  Retain AAMA 2604 or AAMA 2605 for high- or superior-performance organic coatings, respectively, on extrusions and panels.  If specific products are required, name coating manufacturers and products.

G. High-Performance Organic Finish:  2-coat fluoropolymer finish complying with [AAMA 2604] [AAMA 2605] and containing not less than [50] [70] percent PVDF resin by weight in color coat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

H. High-Performance Organic Finish:  [3] [4]-coat fluoropolymer finish complying with AAMA 2605 and containing not less than [50] [70] percent PVDF resin by weight in both color coat and clear topcoat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

2.14 GALVANIZED-STEEL SHEET FINISHES

Some louvers are made from coil-coated metal sheet and are touched up after assembly.  Finishing galvanized steel after fabrication provides better corrosion protection.  Usually retain first paragraph below unless cost is primary consideration.

A. Finish louvers after assembly.

B. Surface Preparation:  Clean surfaces with nonpetroleum solvent so surfaces are free of oil and other contaminants.  After cleaning, apply a conversion coating suited to the organic coating to be applied over it.  Clean welds, mechanical connections, and abraded areas and repair according to ASTM A 780.

C. Baked-Enamel or Powder-Coat Finish:  Immediately after cleaning and pretreating, apply manufacturer's standard 2-coat, baked-on finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat.  Comply with coating manufacturer's written instructions for applying and baking to achieve a minimum dry film thickness of 2 mils (0.05 mm).

1. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

For exact finish, insert names of coating manufacturers and products.

2.15 STAINLESS-STEEL SHEET FINISHES

Delete this article if no stainless-steel, formed-metal louvers.

A. Repair sheet finish by grinding and polishing irregularities, weld spatter, scratches, and forming marks to match surrounding finish.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and openings, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Coordinate setting drawings, diagrams, templates, instructions, and directions for installation of anchorages that are to be embedded in concrete or masonry construction.  Coordinate delivery of such items to Project site.

3.3 INSTALLATION

A. Locate and place louvers and vents level, plumb, and at indicated alignment with adjacent work.

B. Use concealed anchorages where possible.  Provide brass or lead washers fitted to screws where required to protect metal surfaces and to make a weathertight connection.

C. Form closely fitted joints with exposed connections accurately located and secured.

D. Provide perimeter reveals and openings of uniform width for sealants and joint fillers, as indicated.

E. Repair finishes damaged by cutting, welding, soldering, and grinding.  Restore finishes so no evidence remains of corrective work.  Return items that cannot be refinished in the field to the factory, make required alterations, and refinish entire unit or provide new units.

F. Protect unpainted galvanized and nonferrous-metal surfaces that will be in contact with concrete, masonry, or dissimilar metals from corrosion and galvanic action by applying a heavy coating of bituminous paint or by separating surfaces with waterproof gaskets or nonmetallic flashing.

G. Install concealed gaskets, flashings, joint fillers, and insulation as louver installation progresses, where weathertight louver joints are required.  Comply with Division 07 Section "Joint Sealants" for sealants applied during louver installation.

3.4 ADJUSTING AND CLEANING

A. Test operation of adjustable louvers and adjust as needed to produce fully functioning units that comply with requirements.

B. Clean exposed surfaces of louvers and vents that are not protected by temporary covering, to remove fingerprints and soil during construction period.  Do not let soil accumulate during construction period.

C. Before final inspection, clean exposed surfaces with water and a mild soap or detergent not harmful to finishes.  Thoroughly rinse surfaces and dry.

D. Restore louvers and vents damaged during installation and construction so no evidence remains of corrective work.  If results of restoration are unsuccessful, as determined by Architect, remove damaged units and replace with new units.

Delete subparagraph below if no factory-applied finish coatings.

1. Touch up minor abrasions in finishes with air-dried coating that matches color and gloss of, and is compatible with, factory-applied finish coating.

END OF SECTION 089000

	LOUVERS AND VENTS
	089000 - 1



