Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
09/03 (R 06/06)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224300 - HEALTHCARE PLUMBING FIXTURES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following medical plumbing fixtures and related components:

Adjust list below to suit Project.

1. Faucets for [lavatories] [showers] [and] [sinks].

2. Laminar-flow, faucet-spout outlets.

3. Flushometers.

4. Toilet seats.

5. Protective shielding guards.

6. Fixture supports.

7. Bedpan washers.

8. Water closets.

9. Lavatories.

10. Individual showers.

11. Patients' combination toilets.

12. Clinical sinks.

13. Plaster sinks.

14. Surgeons' scrub sinks.

15. Surgeons' instrument sinks.

16. Bathing units.

17. Sitz baths.

18. Bedpan washing equipment.

19. Hydrotherapy whirlpools.

20. Outlet boxes.

21. Morgue equipment.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Domestic Water Piping Specialties" for backflow preventers.

2. Division 22 Section "Sanitary Waste Piping Specialties" for floor drains.

3. Division 22 Section "Plumbing Fixtures" for conventional plumbing fixtures.

4. Division 22 Section "Emergency Plumbing Fixtures."

5. Division 22 Section "Drinking Fountains and Water Coolers."

1.3 DEFINITIONS

Retain abbreviations and terms that remain after this Section has been edited.

A. Accessible Medical Plumbing Fixture:  Plumbing fixture that can be approached, entered, and used by people with disabilities.

B. Fitting:  Device that controls the flow of water into or out of the medical plumbing fixture.  Fittings specified in this Section include supplies and stops, faucets and spouts, shower heads, drains and tailpieces, and traps and waste pipes.

C. FRP:  Fiberglass-reinforced plastic.

D. PMMA:  Polymethyl methacrylate (acrylic) plastic.

1.4 SUBMITTALS

A. Product Data:  For each type of medical plumbing fixture indicated.  Include selected fixture and trim, fittings, accessories, appliances, appurtenances, equipment, and supports.  Indicate materials and finishes, dimensions, construction details, and flow-control rates.

B. LEED Submittal:

1. Product Data for Credit WE [2] [3.1] [3.2] [2 and 3.1] [2, 3.1, and 3.2]:  Documentation indicating flow and water consumption requirements.

Retain first paragraph below if fixtures include electrical components and wiring.

C. Shop Drawings:  Diagram power, signal, and control wiring.

D. Operation and Maintenance Data:  For medical plumbing fixtures to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

Revise first paragraph and subparagraph below to suit manufacturers and types of fixtures specified.  No manufacturer makes all types of fixtures, faucets, etc.

A. Source Limitations:  Obtain medical plumbing fixtures, faucets, and other components of each category through one source from a single manufacturer.

1. Exception:  If fixtures, faucets, or other components are not available from a single manufacturer, obtain similar products from other manufacturers specified for that category.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

First paragraph below is appropriate for private commercial projects.  Retain option if required by authorities having jurisdiction.

C. Regulatory Requirements:  Comply with requirements in ICC A117.1, "Accessible and Usable Buildings and Facilities"[; Public Law 90-480, "Architectural Barriers Act"; and Public Law 101-336, "Americans with Disabilities Act";] for plumbing fixtures for people with disabilities.

D. Regulatory Requirements:  Comply with requirements in Public Law 102-486, "Energy Policy Act," about water flow and consumption rates for plumbing fixtures.

E. NSF Standard:  Comply with NSF 61, "Drinking Water System Components--Health Effects," for fixture materials that will be in contact with potable water.

F. Select combinations fixtures and trim, faucets, fittings, and other components that are compatible.

G. Comply with the following applicable standards and other requirements specified for medical plumbing fixtures:

Retain only subparagraphs below that match fixtures, components, and features specified.

1. Enameled, Cast-Iron Fixtures:  ASME A112.19.1M.

2. Plastic Bathtubs:  ANSI Z124.1.

3. Plastic Shower Enclosures:  ANSI Z124.2.

4. Slip-Resistant Bathing Surfaces:  ASTM F 462.

5. Vitreous-China Fixtures:  ASME A112.19.2M.

H. Comply with the following applicable standards and other requirements specified for [lavatory] [and] [sink] faucets:

Retain only subparagraphs below that match faucets, components, and features specified.

1. Backflow Protection Devices for Faucets with Hose-Thread Outlet:  ASME A112.18.3M.

2. Diverter Valves for Faucets with Hose Spray:  ASSE 1025.

3. Faucets:  ASME A112.18.1.

4. Hose-Connection Vacuum Breakers:  ASSE 1011.

5. Hose-Coupling Threads:  ASME B1.20.7.

6. Integral, Atmospheric Vacuum Breakers:  ASSE 1001.

7. NSF Materials:  NSF 61.

8. Pipe Threads:  ASME B1.20.1.

9. Sensor-Actuated Faucets and Electrical Devices:  UL 1951.

10. Supply Fittings:  ASME A112.18.1.

11. Brass Waste Fittings:  ASME A112.18.2.

I. Comply with the following applicable standards and other requirements specified for [bathtub] [and] [shower] faucets:

Retain only subparagraphs below that match faucets, components, and features specified.

1. Backflow Protection Devices for Hand-Held Showers:  ASME A112.18.3M.

2. Combination, Pressure-Equalizing and Thermostatic-Control Antiscald Faucets:  ASSE 1016.

3. Faucets:  ASME A112.18.1.

4. Hand-Held Showers:  ASSE 1014.

5. High-Temperature-Limit Controls for Thermal-Shock-Preventing Devices:  ASTM F 445.

6. Hose-Coupling Threads:  ASME B1.20.7.

7. Manual-Control Antiscald Faucets:  ASTM F 444.

8. Pipe Threads:  ASME B1.20.1.

9. Pressure-Equalizing-Control Antiscald Faucets:  ASTM F 444 and ASSE 1016.

10. Sensor-Actuated Faucets and Electrical Devices:  UL 1951.

11. Thermostatic-Control Antiscald Faucets:  ASTM F 444 and ASSE 1016.

J. Comply with the following applicable standards and other requirements specified for miscellaneous fittings:

Retain only subparagraphs below that match fittings and features specified.

1. Atmospheric Vacuum Breakers:  ASSE 1001.

2. Brass and Copper Supplies:  ASME A112.18.1.

3. Flexible Water Connectors:  ASME A112.18.6.

4. Manual-Operation Flushometers:  ASSE 1037.

5. Sensor-Operation Flushometers:  ASSE 1037 and UL 1951.

6. Brass Waste Fittings:  ASME A112.18.2.

K. Comply with the following applicable standards and other requirements specified for miscellaneous components:

Retain only subparagraphs below that match components and features specified.

1. Grab Bars:  ASTM F 446.

2. Hose-Coupling Threads:  ASME B1.20.7.

3. Off-Floor Fixture Supports:  ASME A112.6.1M.

4. Pipe Threads:  ASME B1.20.1.

5. Plastic Toilet Seats:  ANSI Z124.5.

6. Supply and Drain Protective Shielding Guards:  ICC A117.1.

1.6 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Faucet Washers and O-Rings:  Equal to [10] <Insert number> percent of amount of each type and size installed.

2. Faucet Cartridges and O-Rings:  Equal to [5] <Insert number> percent of amount of each type and size installed.

3. Flushometer Valve, Repair Kits:  Equal to [10] percent of amount of each type installed, but no fewer than 12 of each type.

4. Provide hinged-top wood or metal box, or individual metal boxes, with separate compartments for each type and size of extra materials listed above.

5. Toilet Seats:  Equal to [5] <Insert number> percent of amount of each type installed.

PART 2 -  PRODUCTS

Part 2 articles specify typical medical plumbing fixtures and components.  Retain and edit only those articles applicable to Project.

If applying for LEED certification, retain options in articles below that limit flow rates and usage to those used in the calculation to show water use savings.

2.1 LAVATORY FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type lavatory faucet required.

A. Lavatory Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Bradley Corporation.

c. Chicago Faucets.

d. Delta Faucet Company.

e. Eljer.

f. Elkay Manufacturing Co.

g. Fisher Manufacturing Co.

h. Grohe America, Inc.

i. Just Manufacturing Company.

j. Kohler Co.

k. Moen, Inc.

l. Royal Brass Mfg. Co.

m. Sayco; a Briggs Plumbing Products, Inc. Company.

n. Speakman Company.

o. T & S Brass and Bronze Works, Inc.

p. Zurn Plumbing Products Group; Commercial Brass Operation.

q. <Insert manufacturer's name.>

4. Description:  Faucet for lavatory-type medical plumbing fixture.  Coordinate faucet inlets with supplies, connectors, and fixture holes; coordinate outlet with spout and fixture receptor.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Maximum Flow Rate:  [2.2 gpm (8.3 L/min.)] <Insert value>.

b. Body Material:  [Solid brass] <Insert material>.

c. Finish:  [Polished chrome plate] <Insert finish>.

d. Type:  [Single-control mixing] [Single-valve nonmixing] [Two-handle mixing].

e. Tempering System:  [Not required] [Thermostatic] [Pressure balance].

f. Supply Centers:  [Single hole] [4 inches (102 mm)] [6 inches (152 mm)] [8 inches (203 mm)] [12 inches (305 mm)] [Adjustable] <Insert spacing>.

g. Mounting:  [Deck, exposed] [Deck, concealed] [Back/wall, exposed] [Back/wall, concealed].

h. Handle(s):  [Single lever] [Cross, four arm] [Wrist blade, 4 inches (102 mm)] [Elbow, 6 inches (152 mm)] [Not applicable] <Insert handle type>.

i. Temperature Indicators:  Color-coded for hot and cold water.

j. Inlet(s):  [NPS 3/8 (DN 10) tubing, plain end] [NPS 3/8 (DN 10) tubing, with NPS 1/2 (DN 15) male adaptor] [NPS 1/2 (DN 15) male shank] [NPS 1/2 (DN 15) female shank].

k. Spout:  [Rigid] [Swing] [Rigid gooseneck] [Swivel gooseneck], brass.

l. Spout Outlet:  [Aerator] [Spray] [Laminar flow] [Plain end] [Spray, 0.5 gpm (1.5 L/min.)].

m. Operation:  [Compression, manual] [Noncompression, manual] [Automatic, hard-wired electric sensor] <Insert operation>.

n. Drain:  [Pop up] [See fixture].

2.2 SHOWER FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type shower faucet required.

A. Shower Faucets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Bradley Corporation.

c. Chicago Faucets.

d. Delta Faucet Company.

e. Eljer.

f. Grohe America, Inc.

g. Interbath, Inc.

h. Kohler Co.

i. Lawler Manufacturing Co., Inc.

j. Leonard Valve Company.

k. Moen, Inc.

l. Powers; a Watts Industries Co.

m. Sayco; a Briggs Plumbing Products, Inc. Company.

n. Speakman Company.

o. Symmons Industries, Inc.

p. T & S Brass and Bronze Works, Inc.

q. Zurn Plumbing Products Group; Commercial Brass Operation.

r. <Insert manufacturer's name.>

4. Description:  Faucet for shower-type medical plumbing fixtures.  Include hot- and cold-water indicators; check stops; and shower head, arm, and flange.  Coordinate faucet inlets with supplies.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Maximum Flow Rate:  [2.5 gpm (9.5 L/min.)] <Insert value>, unless otherwise indicated.

b. Body Material:  [Solid brass] <Insert material>.

c. Finish:  [Polished chrome plate] <Insert finish>.

d. Type:  [Thermostatic] [Pressure balance] [Thermostatic and pressure balance] with integral or field-installed check stops on hot- and cold-water supplies.

e. Mounting:  [Exposed] [Concealed].

f. Handle(s):  [Single lever] [Cross, four arm] [Not applicable] <Insert handle type>.

g. Temperature Indicators:  Color-coded for hot and cold water.

h. Diverter Valve:  [Not required] [Integral with mixing valve] [Not integral with mixing valve].

i. Backflow Protection Device for Hand-Held Shower:  [Required] [Not required].

j. Operation:  [Compression, manual] [Noncompression, manual] [Automatic, hard-wired electric sensor] <Insert operation>.

k. Antiscald Device:  [Integral with mixing valve] [Not required].

l. Supply Connections:  [NPS 1/2 (DN 15)] [NPS 1/2 (DN 15), union] [Sweat].

m. Shower Head Material:  Brass with chrome-plated finish.

n. Head Type:  [Ball joint] [Without ball joint] [Hand held, slide-bar mounted] [Hand held, hook mounted].

o. Spray Pattern:  [Fixed] [Adjustable].

p. Integral Volume Control:  [Required] [Not required].

q. Shower-Arm, Flow-Control Fitting:  [Not required] [1.5 gpm (5.7 L/min.)] [2.0 gpm (7.6 L/min.)].

2.3 SINK FAUCETS

Copy and edit paragraph and subparagraphs in this Article for each type sink faucet required.

A. Sink Faucets, <Insert Drawing Designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Chicago Faucets.

c. Delta Faucet Company.

d. Eljer.

e. Elkay Manufacturing Co.

f. Fisher Manufacturing Co.

g. Grohe America, Inc.

h. Just Manufacturing Company.

i. Kohler Co.

j. Moen, Inc.

k. Royal Brass Mfg. Co.

l. Sayco; a Briggs Plumbing Products, Inc. Company.

m. Speakman Company.

n. T & S Brass and Bronze Works, Inc.

o. Zurn Plumbing Products Group; Commercial Brass Operation.

p. <Insert manufacturer's name.>

4. Description:  Faucet for sink-type medical plumbing fixtures.  Coordinate faucet inlets with supplies and fixture holes; coordinate outlet with spout and fixture receptor.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Maximum Flow Rate:  [2.5 gpm (9.5 L/min.)] <Insert value>, unless otherwise indicated.

b. Body Material:  [Solid brass] <Insert material>.

c. Finish:  [Polished chrome plate] [or] [rough chrome plate] <Insert finish>.

d. Type:  [Sink faucet] [Clinical-sink faucet with stops in shanks, vacuum breaker, hose-thread outlet, and pail hook] <Insert type>.

e. Tempering Device:  [Thermostatic] [Pressure balance] [Not required].

f. Mixing Valve:  [Single control] [Two-lever handle].

g. Backflow Protection Device for Hose Outlet:  [Required] [Not required] [Not applicable].

h. Supply Centers:  [Single hole] [4 inches (102 mm)] [6 inches (152 mm)] [8 inches (203 mm)] [Adjustable] <Insert spacing>.

i. Mounting:  [Deck, exposed] [Deck, concealed] [Back/wall, exposed] [Back/wall, concealed].

j. Handle(s):  [Lever] [Knob] [Cross, four arm] [Wrist blade, 4 inches (102 mm)] [Elbow, 6 inches (152 mm)] [Not applicable].

k. Temperature Indicators:  Color-coded for hot water on left and cold water on right.

l. Inlet(s):  [NPS 3/8 (DN 10) plain-end tubing] [NPS 3/8 (DN 10) tubing with NPS 1/2 (DN 15) male adapter] [NPS 1/2 (DN 15) male shank] [NPS 1/2 (DN 15) female shank].

m. Spout:  [Rigid, solid] [Swing tubular] [Rigid, gooseneck, solid] [Swivel, gooseneck, solid] brass[ with wall brace].

n. Spout Outlet:  [Aerator] [Swivel aerator/spray] [Spray] [Laminar flow] [Hose thread] [Plain end].

o. Vacuum Breaker:  [Required] [Not required].

p. Operation:  [Compression, manual] [Noncompression, manual] [Automatic, hard-wired electric sensor] <Insert operation>.

2.4 LAMINAR-FLOW FAUCET-SPOUT OUTLETS

Spout outlets in this Article are non-aerating, produce less splashing than conventional faucet spouts, and help reduce bacteria growth.  They may be used on bathtub-filler, lavatory, shower, and sink spouts.

Copy and edit paragraph and subparagraphs in this Article for each type of faucet-spout outlet required.

A. Laminar-Flow Faucet-Spout Outlets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Chronomite Laboratories, Inc.

b. NEOPERL, Inc.

c. <Insert manufacturer's name.>

4. Description:  Chrome-plated-brass faucet-spout outlet that produces non-aerating laminar stream.  Include male or female thread that mates with faucet outlet for attachment to faucets where indicated and flow-rate range that includes flow of faucet.

2.5 FLUSHOMETERS

Copy and edit paragraph and subparagraphs in this Article for each type flushometer required.

A. Flushometers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Coyne & Delany Co.

b. Delta Faucet Company.

c. Sloan Valve Company.

d. Zurn Plumbing Products Group; Commercial Brass Operation.

e. <Insert manufacturer's name.>

4. Description:  Flushometer for [clinical-sink] [water-closet]-type medical plumbing fixture.  Include brass body with corrosion-resistant internal components,[ non-hold-open feature,] control stop with check valve, vacuum breaker, and copper or brass tubing, and polished chrome-plated finish on exposed parts.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Internal Design:  Diaphragm operation.

b. Style:  [Exposed] [Concealed].

c. Inlet Size:  NPS 1 (DN 25).

d. Trip Mechanism:  [Oscillating, lever-handle actuator] [Mechanical, push-button actuator with stainless-steel access plate] [Hydraulic, push-button actuator] [Foot-pedal actuator] [Hard-wired, electric-sensor actuator] [Battery-operated sensor actuator] <Insert type>.

e. Consumption:  [1.6 gal./flush (6.0 L/flush)] [3.5 gal./flush (13.3 L/flush)] <Insert value>.

f. Tailpiece Size:  [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] <Insert size> and [standard] <Insert dimension> length to top of bowl.

g. Integral Bedpan Washer:  [Not required] [Factory fabricated, attached to tailpiece, and with spray head].

2.6 TOILET SEATS

Copy and edit paragraph and subparagraphs in this Article for each type toilet seat required.

A. Toilet Seats, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bemis Manufacturing Company.

b. Centoco Manufacturing Corp.

c. Church Seats.

d. Olsonite Corp.

e. Sanderson Plumbing Products, Inc.; Beneke Div.

f. Sperzel.

g. <Insert manufacturer's name.>

4. Description:  Plastic toilet seat for water-closet-type medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Material:  Molded, solid plastic[ with antimicrobial agent].

b. Configuration:  [Closed] [Open] front [with] [without] cover.

c. Size:  Elongated, unless otherwise indicated.

d. Class:  [Standard] [Heavy-duty] commercial.

e. Hinge Type:  Stainless-steel [CK, check] [SC, self-sustaining check] <Insert type>.

f. Color:  [White] [Black].

2.7 PROTECTIVE SHIELDING GUARDS

A. Protective Shielding Pipe Covers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Engineered Brass Co.

b. Insul-Tect Products Co.; a Subsidiary of MVG Molded Products.

c. McGuire Manufacturing Co., Inc.

d. Plumberex Specialty Products Inc.

e. TCI Plumbing Products, Inc.

f. TRUEBRO, Inc.

g. Zurn Plumbing Products Group; Tubular Brass Plumbing Products Operation.

h. <Insert manufacturer's name.>

3. Description:  Manufactured plastic wraps for covering medical plumbing fixture [hot-water supply] [hot- and cold-water supplies] and trap and drain piping.  Comply with Americans with Disabilities Act (ADA) requirements.

B. Protective Shielding Piping Enclosures, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. TRUEBRO, Inc.

b. <Insert manufacturer's name.>

3. Description:  Manufactured plastic enclosure for covering medical plumbing fixture hot- and cold-water supplies and trap and drain piping.  Comply with ADA requirements.

2.8 FIXTURE SUPPORTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Josam Company.

2. MIFAB Manufacturing Inc.

3. Smith, Jay R. Mfg. Co.

4. Tyler Pipe; Wade Div.

5. Watts Drainage Products Inc.; a div. of Watts Industries, Inc.

6. Zurn Plumbing Products Group; Specification Drainage Operation.

7. <Insert manufacturer's name.>

Copy and edit paragraph and subparagraph below for each type water-closet support required.

C. Water-Closet Supports, <Insert drawing designation>:

1. Description:  Combination carrier designed for [accessible] [standard] mounting height of wall-mounting, water-closet-type medical plumbing fixture.  Include single or double, vertical or horizontal, hub-and-spigot or hubless waste fitting as required for piping arrangement; faceplates; couplings with gaskets; feet; and fixture bolts and hardware matching fixture.  Include additional extension coupling, faceplate, and feet for installation in wide pipe space.

Copy and edit paragraph and subparagraphs below for each type lavatory support required.

D. Lavatory Supports, <Insert drawing designation>:

1. Description:  Type [I, lavatory carrier with exposed arms and tie rods] [II, lavatory carrier with concealed arms and tie rod] [III, lavatory carrier with hanger plate and tie rod] for wall-mounting, lavatory-type medical plumbing fixture.  Include steel uprights with feet.

2. Accessible-Fixture Support:  Include rectangular steel uprights.

Copy and edit paragraph and subparagraph below for each type sink support required.

E. Sink Supports, <Insert drawing designation>:

1. Description:  Type [I, sink carrier with exposed arms and tie rods] [II, sink carrier with hanger plate, bearing studs, and tie rod] [III, sink carrier with hanger plate and exposed arms] for sink-type medical plumbing fixture.  Include steel uprights with feet.

2.9 BEDPAN WASHERS

Refer to "Flushometers" Article for flushometer-valve, mounted-type bedpan washers.

Copy and edit paragraph and subparagraphs in this Article for each type bedpan washer required.

A. Bedpan Washers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. American Standard Companies, Inc.

c. Chicago Faucets.

d. Crane Plumbing, L.L.C./Fiat Products.

e. Delta Faucet Company.

f. Eljer.

g. Kohler Co.

h. Royal Brass Mfg. Co.

i. T & S Brass and Bronze Works, Inc.

j. Zurn Plumbing Products Group; Commercial Brass Operation.

k. <Insert manufacturer's name.>

4. Description:  Wall-mounting, hand-held, [hand-control] [single-pedal, foot-control] [double-pedal, hot- and cold-water control], medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Hose:  [48-inch- (1220-mm-)] <Insert length> long rubber or vinyl hose with spray nozzle, wall bracket, and hook.

b. Self-closing valve.

c. Loose-key supply stop.

d. Vacuum Breaker:  Wall mounting, atmospheric.

e. Finish:  Polished, chrome-plated finish on metal parts exposed after installation.

2.10 WATER CLOSETS

Copy and edit paragraph and subparagraphs below for each type wall-mounting, back-outlet water closet required.

A. Wall-Mounting Water Closets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

4. Description:  [Accessible, wall] [Wall]-mounting, back-outlet, vitreous-china medical plumbing fixture designed for bedpan washing and flushometer valve operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in five subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Style:  Flushometer valve.

1) Bowl Type:  Elongated with siphon-jet design and bedpan lugs or slots.

2) Design Consumption:  [1.6 gal./flush (6 L/flush)] <Insert value>.

3) Color:  White.

b. Flushometer:  <Insert designation.>

c. Toilet Seat:  <Insert designation.>

d. Fixture Support:  Water-closet support <Insert designation> combination carrier.

Retain subparagraph below if separate bedpan washer is required.

e. Bedpan Washer:  <Insert designation.>

Copy and edit paragraph and subparagraphs below for each type floor-mounting, floor-outlet water closet required.

B. Floor-Mounting Water Closets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C/Fiat Products.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

4. Description [Accessible, floor] [Floor]-mounting, floor-outlet, vitreous-china medical plumbing fixture designed for bedpan washing and flushometer valve operation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in four subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Style:  Flushometer valve.

1) Bowl Type:  Elongated with siphon-jet design and bedpan lugs or slots.  Include bolt caps matching fixture.

2) Height:  [Standard] [Accessible].

3) Design Consumption:  [1.6 gal./flush (6 L/flush)] <Insert value>.

4) Color:  White.

b. Flushometer:  <Insert designation.>

c. Toilet Seat:  <Insert designation.>

Retain subparagraph below if separate bedpan washer is required.

d. Bedpan Washer:  <Insert designation.>

2.11 LAVATORIES

Copy and edit paragraph and subparagraphs below for each type wall-mounting lavatory required.

A. Wall-Mounting Lavatories, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Briggs Plumbing Products, Inc.

c. Crane Plumbing, L.L.C./Fiat Products.

d. Eljer.

e. Gerber Plumbing Fixtures LLC.

f. Kohler Co.

g. <Insert manufacturer's name.>

4. Description:  [Accessible, wall] [Wall]-mounting, vitreous-china medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 11 subparagraphs and associated subparagraph below may be reduced or omitted.

a. Type:  [With back] [Ledge back] [Shelf back] [Slab].

b. Size:  [18 by 15 inches (457 by 381 mm)] [19 by 16 inches (483 by 406 mm)] [20 by 18 inches (508 by 457 mm)] [24 by 20 inches (610 by 508 mm)] <Insert dimensions> rectangular.

c. Faucet Hole Punching:  [One hole] [Three holes, 2-inch (51-mm) centers] [Three holes, 4-inch (102-mm) centers] <Insert spacing>.

d. Faucet Hole Location:  [Top] [Front wall] [Inclined panel].

e. Color:  White.

f. Faucet:  Lavatory <Insert designation> [with pop-up waste] [for separate drain].

g. Supplies:  NPS 3/8 (DN 10) chrome-plated copper tubes[ or flexible connectors] with stops.

h. Drain:  [See faucet] [Grid] [Grid with offset].

1) Location:  [Not applicable] <Insert distance from front edge>.

i. Drain Piping:  [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [0.032-inch- (0.8-mm-)] [0.045-inch- (1.1-mm-)] thick tubular brass waste to wall; and wall escutcheon.

j. Protective Shielding Guard(s):  <Insert designation.>

k. Fixture Support:  Lavatory <Insert designation>.

Copy and edit paragraph and subparagraphs below for each type counter-mounting lavatory required.

B. Counter-Mounting Lavatories, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Briggs Plumbing Products, Inc.

c. Crane Plumbing, L.L.C./Fiat Products.

d. Eljer.

e. Gerber Plumbing Fixtures LLC.

f. Kohler Co.

g. <Insert manufacturer's name.>

4. Description:  [Accessible,] [Counter-mounting] [Undercounter-mounting], vitreous-china, medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Type:  [Flat rim with ledge] [Self-rimming].

Retain one of first three subparagraphs below.

b. Rectangular Lavatory Size:  [18 by 15 inches (457 by 381 mm)] [19 by 16 inches (483 by 406 mm)] [20 by 18 inches (508 by 457 mm)] [24 by 20 inches (610 by 508 mm)] <Insert dimensions>.

c. Oval Lavatory Size:  [19 by 16 inches (483 by 406 mm)] [20 by 17 inches (508 by 432 mm)] <Insert dimensions>.

d. Round Lavatory Size:  [18 inches (457 mm)] [19 inches (483 mm)] <Insert dimension> in diameter.

e. Faucet Hole Punching:  [One hole] [Three holes, 2-inch (51-mm) centers] [Three holes, 4-inch (102-mm) centers].

f. Faucet Hole Location:  [Top] [Front wall] [Inclined panel].

g. Color:  White.

h. Faucet:  Lavatory <Insert designation> [with pop-up waste] [for separate drain].

i. Supplies:  NPS 3/8 (DN 10) chrome-plated copper tubes[ or flexible connectors] with stops.

j. Drain:  [See faucet] [Grid] [Grid with offset].

1) Location:  [Not applicable] <Insert distance from front edge>.

k. Drain Piping:  [NPS 1-1/4 (DN 32)] [NPS 1-1/4 by NPS 1-1/2 (DN 32 by DN 40)] chrome-plated, cast-brass P-trap; [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [0.032-inch- (0.8-mm-)] [0.045-inch- (1.1-mm-)] thick tubular brass waste to wall; and wall escutcheon.

l. Protective Shielding Guard(s):  <Insert designation.>

2.12 INDIVIDUAL SHOWERS

Copy and edit paragraph and subparagraphs below for each type individual shower enclosure required.

A. Individual Showers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acryline USA, Inc.

b. Aker Plastics Co., Inc.

c. Aqua Bath Company, Inc.

d. Aqua Glass Corporation.

e. Clarion Bathware.

f. Crane Plumbing, L.L.C./Fiat Products.

g. Fiberglass Systems, Inc.

h. Florestone Products Co., Inc.

i. Invacare Corp.; Invacare Continuing Care Group; Silcraft Corp. Div.

j. Kohler Co.

k. LASCO Bathware.

l. Praxis Industries, Inc., Aquarius Products.

m. <Insert manufacturer's name.>

4. Description:  [Accessible, ][FRP] [PMMA] shower enclosure medical plumbing fixture with slip-resistant bathing surface complying with ASTM F 462.  Comply with ADA requirements for use by people with disabilities.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Size:  [36 by 34 inches (915 by 865 mm)] [42 by 36 inches (1065 by 915 mm)] [43 by 39 inches (1090 by 990 mm)] [48 by 34 inches (1220 by 865 mm)] [52 by 36 inches (1320 by 915 mm)] [60 by 36 inches (1525 by 915 mm)] [72 by 36 inches (1830 by 915 mm)] <Insert dimensions>.

b. Surround:  One piece.

c. Color:  [White] <Insert color>.

d. Faucet:  Shower <Insert designation>.

e. Drain:  Grid, NPS 2 (DN 50).

1) Location:  [Left side] [Center] [Right side].

f. Accessories:  If not furnished as integral components of specified fixture.  Accessories are specified in Division 10 Section "Toilet, Bath, and Laundry Accessories."

1) Grab bar(s).

2) [Normal] [Heavy]-duty shower-curtain rod.

3) [Vinyl] [Duck] [Antibacterial] shower curtain.

4) Shower-curtain hooks.

Retain subparagraph below if required.

5) Folding seat.

2.13 PATIENTS' COMBINATION TOILETS

Copy and edit paragraph and subparagraphs below for each type swing-away, patients' combination toilet required.

A. Swing-Away, Patients' Combination Toilets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Metcraft Industries Inc.

c. Whitehall Manufacturing; a division of Acorn Engineering Company.

d. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, combination water closet and lavatory medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in four subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet:  Fixed installation with storage space and toilet paper holder.

1) Material:  [Stainless steel] [Stainless steel, plastic laminate, or fiberglass] with [laminated-wood or -plastic] [solid-plastic] [stainless-steel] top surface.

2) Color:  [Not applicable] <Insert color>.

3) Mounting:  Wall bracket.

b. Water Closet:  Swivel, floor-mounting, [back] [floor]-outlet, flushometer valve design.

1) Material:  Stainless steel.

2) Orientation:  [Left] [Right] hand.

3) Color:  [Not applicable] <Insert color>.

4) Toilet Seat:  White, solid plastic.

5) Flushometer:  Concealed flushometer valve with push-button trip mechanism, check stop, and vacuum breaker on tailpiece.

6) Fixture Support:  Floor plate.

7) Seal:  For outlet.

c. Lavatory:  Counter mounting.

1) Material:  [Stainless steel] <Insert material>.

2) Color:  [Not applicable] <Insert color>.

3) Faucet:  [Gooseneck type with wrist-blade handles] [Swing-spout type with single lever] <Insert type>.

4) Drain:  Grid, NPS 1-1/4 (DN 32).

5) Drain Piping:  NPS 1-1/4 (DN 32) chrome-plated, cast-brass P-trap; tubular-brass waste to wall; and wall flange.

d. Bedpan Washer:  On flushometer valve tailpiece or separate attachment affixed to unit.

Copy and edit paragraph and subparagraphs below for each type static, patients' combination toilet required.

B. Static, Patients' Combination Toilets, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Bradley Corporation.

b. Hill-Rom Services, Inc.

c. Whitehall Manufacturing; a division of Acorn Engineering Company.

d. <Insert manufacturer's name.>

4. Description:  Factory-fabricated, combination water closet and lavatory fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in four subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet:  Fixed installation; swing-away cabinet or retractable, water-closet cover design with storage space and toilet paper holder.

1) Material:  [Stainless steel] [Stainless steel, plastic laminate, or fiberglass] with [laminated-wood or -plastic] [solid-plastic] [stainless-steel] top surface.

2) Color:  [Not applicable] <Insert color>.

3) Mounting:  Wall bracket.

b. Water Closet:  Floor-mounting, floor-outlet, flushometer valve design.

1) Material:  Stainless steel or vitreous china.

2) Orientation:  [Left] [Right] hand.

3) Color:  [Not applicable] <Insert color>.

4) Toilet Seat:  White, solid plastic.

5) Flushometer:  Concealed flushometer valve with push-button trip mechanism, check stop, and vacuum breaker on tailpiece.

6) Seal:  For outlet.

c. Lavatory:  Counter mounting.

1) Material:  [Stainless steel] <Insert material>.

2) Color:  [Not applicable] <Insert color>.

3) Faucet:  [Gooseneck type with wrist-blade handles] [Swing-spout type with single lever] <Insert type>.

4) Drain:  Grid, NPS 1-1/4 (DN 32).

5) Drain Piping:  NPS 1-1/4 (DN 32) chrome-plated, cast-brass P-trap; tubular-brass waste to wall; and wall flange.

d. Bedpan Washer:  On flushometer valve tailpiece or separate attachment affixed to unit.

2.14 CLINICAL SINKS

Copy and edit paragraph and subparagraphs below for each type wall-mounting clinical sink required.

A. Wall-Mounting Clinical Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

4. Description:  Wall-mounting, back-outlet, vitreous-china, flushing-rim, service-sink-type medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs below may be reduced or omitted.

a. Size:  Approximately 25 by 20 inches (635 by 510 mm).

b. Color:  White.

c. Rim Guard:  Stainless steel on front and also on sides if flat rim.

Use polished, chrome-plated, solid-brass, service-sink faucet type in first subparagraph below.  Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

d. Faucet:  Sink <Insert designation>.

e. Flushometer:  <Insert designation.>

f. Bedpan Washer:  <Insert designation.>

g. Fixture Support:  Sink <Insert designation>.

Copy and edit paragraph and subparagraphs below for each type floor-mounting clinical sink required.

B. Floor-Mounting Clinical Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Eljer.

d. Kohler Co.

e. <Insert manufacturer's name.>

Caution:  This fixture may require a raised base to attain correct height.  Verify with manufacturer.

4. Description:  Floor-mounting, bottom-outlet, vitreous-china, flushing-rim, service-sink-type medical plumbing fixture.  Include bolt caps.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  Approximately 27 by 20 inches (685 by 510 mm).

b. Color:  White.

c. Rim Guards:  Stainless steel on front and sides.

d. Sink Base:  10-inch (25.4-mm) -high, cast terrazzo if required.

Use polished, chrome-plated, solid-brass, service-sink faucet type in first subparagraph below.  Include integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook.

e. Faucet:  Sink <Insert designation>.

f. Flushometer:  <Insert designation.>

g. Bedpan Washer:  <Insert designation.>

2.15 PLASTER SINKS

Copy and edit paragraph and subparagraphs in this Article for each type plaster sink required.

A. Plaster Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Kohler Co.

d. <Insert manufacturer's name.>

4. Description:  Wall-mounting, vitreous-china medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Size:  [24 by 22 inches (610 by 560 mm)] [30 by 22 inches (760 by 560 mm)] with back or ledge faucet holes.

b. Color:  White.

c. Faucet Holes:  [One] [Two] in back or ledge.

d. Faucet:  Sink <Insert designation>.

e. Supplies:  NPS 1/2 (DN 15) chrome-plated copper tubes[ or flexible connectors] with stops.

Pipe sizes in first three subparagraphs and associated subparagraphs below must be coordinated.

f. Drain:  Grid, NPS 1-1/2 (DN 40)[ with NPS 1-1/2 (DN 40) to NPS 2 (DN 50) adaptor].

g. Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] chrome-plated brass; 0.045-inch- (1.1-mm-) thick waste to interceptor; interceptor to wall; and wall flange.

h. Plaster Interceptor:

1) Basis-of-Design Product:  <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a) Josam Company.

b) MIFAB Manufacturing Inc.

c) Smith, Jay R. Mfg. Co.

d) Tyler Pipe; Wade Div.

e) Watts Drainage Products Inc.; a div. of Watts Industries, Inc.

f) Zurn Plumbing Products Group; Specification Drainage Operation.

g) <Insert manufacturer's name.>

2) Description:  Cast-iron or steel body and removable cover with acid-resistant-enameled interior lining and outside coating; removable, corrosion-resistant metal screens or strainer; and [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] inlet and outlet.

5. Fixture Support:  Sink <Insert designation> with white-enameled-steel brackets.

2.16 SURGEONS' SCRUB SINKS

Copy and edit paragraph and subparagraphs below for each type stainless-steel surgeons' scrub sink required.

A. Stainless-Steel Surgeons' Scrub Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Jewett.

c. Just Manufacturing Company.

d. Medicom, A. R. Inc.

e. Whitehall Manufacturing; a division of Acorn Engineering Company.

f. <Insert manufacturer's name.>

4. Description:  Wall-mounting, sink-type medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  Approximately 31 by 20 inches (790 by 510 mm) with back with 1 faucet hole.

b. Faucet:  Chrome-plated-brass, gooseneck type matching fixture.

c. Operation:  [Foot-pedal] [Knee] [Automatic, hard-wired electric sensor] control.

d. Supplies:  NPS 1/2 (DN 15) chrome-plated copper tubes[ or flexible connectors] with stops.

e. Drain:  Grid, NPS 1-1/2 (DN 40).

f. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular-brass waste to wall; and wall flange.

g. Fixture Support:  Sink <Insert designation>.

Copy and edit paragraph and subparagraphs below for each type vitreous-china surgeons' scrub sink required.

B. Vitreous-China Surgeons' Scrub Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. American Standard Companies, Inc.

b. Crane Plumbing, L.L.C./Fiat Products.

c. Kohler Co.

d. <Insert manufacturer's name.>

4. Description:  Wall-mounting, sink-type medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  [28 by 22 inches (710 by 560 mm)] [30 by 22 inches (760 by 560 mm)] <Insert dimensions> with back or ledge with 1 faucet hole.

b. Color:  White.

c. Faucet:  Chrome-plated-brass, gooseneck-type matching fixture.

d. Operation:  [Foot-pedal] [Knee] control.

e. Supplies:  NPS 1/2 (DN 15) chrome-plated copper tubes[ or flexible connectors] with stops.

f. Drain:  Grid, NPS 1-1/2 (DN 40).

g. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular-brass waste to wall; and wall flange.

h. Fixture Support:  Sink <Insert designation>.

2.17 SURGEONS' INSTRUMENT SINKS

Copy and edit paragraph and subparagraphs in this Article for each type surgeons' instrument sink required.

A. Surgeons' Instrument Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Just Manufacturing Company.

c. <Insert manufacturer's name.>

4. Description:  Wall-mounting, stainless-steel, sink-type medical plumbing fixture.  Include instrument tray on each side.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  28 by 20 inches (710 by 510 mm) with 1 hole for deck-mounting faucet.

b. Faucet:  Chrome-plated-brass, gooseneck type matching fixture with [knee] [foot-pedal] control for mixing hot- and cold-water supplies.

c. Supplies:  NPS 1/2 (DN 15) chrome-plated copper tubes[ or flexible connectors] with stops.

d. Drain:  Grid, NPS 1-1/2 (DN 40).

e. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular-brass waste to wall; and wall flange.

f. Fixture Support:  Sink <Insert designation>.

2.18 BATHING UNITS

Caution:  Provide one or more floor drains near bathing units.

Copy and edit paragraph and subparagraphs below for each type institutional bath tub required.

A. Institutional Bath Tubs, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Eljer.

b. Kohler Co.

c. <Insert manufacturer's name.>

4. Description:  Enameled, cast-iron, island medical plumbing fixture with separate wall-mounting faucet.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  66 by 30 by 18 inches (1680 by 765 by 455 mm).

b. Base:  Enameled, cast iron to raise rim of bathtub to 28 inches (710 mm) above the floor.

c. Faucet:  [Shower] [Sink] <Insert designation> modified to include tub filler spout.

d. Supplies:  NPS 1/2 (DN 15) chrome-plated copper tubes[ or flexible connectors] with stops.  Include atmospheric vacuum breaker.

e. Drain:  NPS 1-1/2 (DN 40); chrome-plated exposed parts; brass pop-up waste and overflow.

f. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; 0.045-inch- (1.1-mm-) thick tubular-brass waste to wall; and wall flange.

Copy and edit paragraph and subparagraphs below for each type bathing unit required.

B. Bathing Units, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ARJO.

b. Invacare Corp.; Invacare Continuing Care Group; Silcraft Corp. Div.

c. <Insert manufacturer's name.>

4. Description:  Plastic-tub, institutional side-entry [whirlpool-]bath fixture with integral controls.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Tub Size:  [60 by 30 inches (1525 by 765 mm)] <Insert dimensions>.

b. Controls:  Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

c. Supplies:  [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing with ball, gate, or globe valves.

d. Drain:  [NPS 1-1/2 (DN 40)] [and] [NPS 2 (DN 50)].

e. Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] cast-brass P-trap, waste to wall, and wall flange.  Include combined drain piping if two drains.

f. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Bathing units in paragraph below may require additional data for optional features or special applications.

Copy and edit paragraph and subparagraphs below for each type bathing unit required.

C. Bathing Units, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ARJO.

b. Clarion Bathware.

c. Invacare Corp.; Invacare Continuing Care Group; Silcraft Corp. Div.

d. <Insert manufacturer's name.>

4. Description:  Plastic-tub, institutional [side] [transfer-lift] [slide-on]-entry, [adjustable] [fixed]-height bath fixture with integral controls.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Tub Size:  [60 by 30 inches (1525 by 765 mm)] <Insert dimensions>.

b. Controls:  Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

c. Supplies:  [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing with ball, gate, or globe valves.

d. Drain:  [NPS 1-1/2 (DN 40)] [and] [NPS 2 (DN 50)].

e. Drain Piping:  [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)] cast-brass P-trap, waste to wall, and wall flange.  Include combined drain piping if two drains.

f. Lift System:  [Not required] <Insert description>.

g. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type bathing unit required.

D. Bathing Units, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ARJO.

b. Invacare Corp.; Invacare Continuing Care Group; Silcraft Corp. Div.

c. <Insert manufacturer's name.>

4. Description:  Plastic-tub, institutional front-entry shower fixture with integral controls.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet Size:  [35 by 41 inches (889 by 1041 mm)] <Insert dimensions>.

b. Controls:  Vacuum breakers on supplies, thermostatic mixing valve, tub fill spout, and hand-held shower head.

c. Supplies:  [NPS 3/4 (DN 20)] [NPS 1 (DN 25)] copper tubing with ball, gate, or globe valves.

d. Drain:  NPS 2 (DN 50).

e. Drain Piping:  NPS 2 (DN 50) cast-brass P-trap, waste to wall, and wall flange.

f. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type residential bath tub required.

E. Residential Bath Tubs, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. BathEase Inc.

b. Invacare Corp.; Invacare Continuing Care Group; Silcraft Corp. Div.

c. Premier Bathrooms.

d. <Insert manufacturer's name.>

4. Description:  Plastic island[ or against-wall-installation] medical plumbing fixture with side door, seat, and separate wall-mounting faucet.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in subparagraphs below may be reduced or omitted.

a. Size:  Approximately 60 by 32 by 21 inches (1525 by 815 by 535 mm).

b. Seat:  Integral.

c. Drain Location:  [Left] [Right] end.

Retain three subparagraphs above or below.

d. Size:  Approximately 60 by 42 by 24.5 inches (1525 by 1070 by 620 mm).

e. Seat:  [Integral bench] [None].

f. Drain Location:  Right end.

Retain subparagraphs below with either "Size" Subparagraph retained above.

g. Material:  PMMA.

h. Skirt:  [Front only] [Full, on three sides].

i. Door:  Side opening with rubber sealing gasket.

j. Faucet:  [Shower] [Sink] <Insert designation> modified to include tub filler spout.

k. Supplies:  NPS 1/2 (DN 15) chrome-plated copper tubes[ or flexible connectors] with stops.  Include atmospheric vacuum breaker.

l. Drain:  NPS 1-1/2 (DN 40); chrome-plated exposed parts; brass pop-up waste and overflow.

m. Drain Piping:  NPS 1-1/2 (DN 40) cast-brass P-trap and 0.045-inch- (1.1-mm-) thick, tubular-brass waste to wall.

2.19 SITZ BATHS

Copy and edit paragraph and subparagraphs in this Article for each type sitz bath required.

A. Sitz Baths, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Crane Plumbing, L.L.C./Fiat Products.

b. Eljer.

c. Kohler Co.

d. <Insert manufacturer's name.>

4. Description:  [Pedestal] [Wall]-mounting, vitreous-china, perineal bath medical plumbing fixture.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Color:  White.

b. Drain:  NPS 1-1/2 (DN 40) with removable overflow attachment.

c. Drain Piping:  NPS 1-1/2 (DN 40) chrome-plated, cast-brass P-trap; waste to wall; and wall flange.

d. Fixture Support:  Sink <Insert designation>.

e. Faucet:

1) Basis-of-Design Product:  <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a) Lawler Manufacturing Co., Inc.

b) Leonard Valve Company.

c) Powers; a Watts Industries Co.

d) Symmons Industries, Inc.

e) <Insert manufacturer's name.>

2) Description:  Wall-mounting, single-lever-handle, thermostatic-mixing-valve faucet with concealed supplies and wall-mounting thermometer.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in first four subparagraphs below may be reduced or omitted.

a) Material:  Brass body and escutcheon.

b) Flow Rate:  Modified to [1.5 gpm (5.7 L/min.)] <Insert value> maximum, unless otherwise indicated.

c) Finish:  Polished chrome plate.

d) Temperature Indicators:  Color-coded for hot and cold water.

f. Exposed Piping:  Chrome-plated; brass pipe or copper tube.

2.20 BEDPAN WASHING EQUIPMENT

Units in this Article require an atmospheric and a sanitary vent.  Do not connect atmospheric vent to sanitary vent piping.

Copy and edit paragraph and subparagraphs below for each type bedpan washer/sanitizer required.

A. Bedpan Washers/Sanitizers, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. STERIS Corporation.

b. <Insert manufacturer's name.>

4. Description:  [Recessed] [On-wall] [Pedestal]-mounting medical plumbing fixture for cleaning bedpans and urinals having cast-iron chamber and waste assembly with spray nozzles and [enameled] [stainless]-steel front panel and cover box.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Controls:  Electric, 120-V ac, automatic operation with timer, solenoid valves, and circuit breaker.

b. Door Mechanism:  Foot-pedal operation.

c. Supplies:  NPS 1 (DN 25) cold water and NPS 3/8 (DN 10) [hot water] [steam].

d. Drain:  NPS 3 (DN 80) P-trap and soil pipe.

e. Atmospheric Vent:  NPS 2 (DN 50).

f. Mounting Hardware:  Matching fixture mounting arrangement.

g. Accessories:

1) Bedpan Rack(s):  [One] [Two] <Insert number>.

2) Urinal Rack(s):  [One] [Two] <Insert number>.

3) Drain Tray(s):  [One] [Two] <Insert number>.

Copy and edit paragraph and subparagraphs below for each type bedpan washer/disinfector required.

B. Bedpan Washers/Disinfectors, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ARJO.

b. <Insert manufacturer's name.>

4. Description:  [Freestanding] [On-wall] [Undercounter]-mounting medical plumbing fixture for cleaning bedpans and urinals; with steam generator, pump, and spray nozzle.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Controls:  Electric, automatic operation.

b. Cabinet:  Stainless steel.

c. Wash Chamber:  Stainless steel.

d. Supplies:  NPS 1/2 (DN 15) cold water and NPS 1/2 (DN 15) hot water.

e. Drain:  NPS 4 (DN 100) P-trap and soil pipe.

f. Mounting Hardware:  Matching fixture mounting arrangement.

g. Unit Electrical Characteristics:

1) Volts:  [208] [240] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

2.21 HYDROTHERAPY WHIRLPOOLS

Copy and edit paragraph and subparagraphs below for each type podiatry whirlpool required.

A. Podiatry Whirlpools, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ferno Ille; a div. of Ferno-Washington, Inc.

b. Whitehall Manufacturing; a division of Acorn Engineering Company.

c. <Insert manufacturer's name.>

4. Description:  Stationary, stainless-steel tank for feet and ankles.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Water Capacity:  15 gal. (57 L).

b. Drain:  Waste connection.

c. Controls.

d. Thermometer:  Control panel or tank mounted.

e. One electric turbine ejector.

f. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type upper-extremity whirlpool required.

B. Upper-Extremity Whirlpools, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ferno Ille; a div. of Ferno-Washington, Inc.

b. Whitehall Manufacturing; a division of Acorn Engineering Company.

c. <Insert manufacturer's name.>

4. Description:  Stationary, pedestal-mounted, stainless-steel tank for arms, hands, and elbows.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Water Capacity:  25 gal. (95 L).

b. Drain:  Waste connection.

c. One arm support.

d. Controls.

e. Thermometer:  Control panel or tank mounted.

f. One electric turbine ejector.

g. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type high-tank body whirlpool required.

C. High-Tank Body Whirlpools, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ferno Ille; a div. of Ferno-Washington, Inc.

b. Whitehall Manufacturing; a division of Acorn Engineering Company.

c. <Insert manufacturer's name.>

4. Description:  Stationary, stainless-steel tank for legs, hip, and back.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Water Capacity:  105 gal. (397 L).

b. Drain:  Waste connection.

c. Controls.

d. Thermometer:  Control panel or tank mounted.

e. One electric turbine ejector.

f. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phases:  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type low-tank body whirlpool required.

D. Low-Tank Body Whirlpools, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ferno Ille; a div. of Ferno-Washington, Inc.

b. Whitehall Manufacturing; a division of Acorn Engineering Company.

c. <Insert manufacturer's name.>

4. Description:  Stationary, extended-length stainless-steel tank for legs, hip, and lower back.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Water Capacity:  105 gal. (397 L).

b. Drain:  Waste connection.

c. Controls.

d. Thermometer:  Control panel or tank mounted.

e. Head rest.

f. One electric turbine ejector.

g. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Copy and edit paragraph and subparagraphs below for each type small, Hubbard immersion tank required.

E. Small, Hubbard Immersion Tanks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ferno Ille; a div. of Ferno-Washington, Inc.

b. Whitehall Manufacturing; a division of Acorn Engineering Company.

c. <Insert manufacturer's name.>

4. Description:  Stationary, butterfly-shaped tank, for full-body massage

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 17 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Tank Dimensions:  [93 by 64 by 22 inches (2362 by 1626 by 560 mm)] <Insert dimensions>.

b. Overall Height:  [34 to 38 inches (864 to 965 mm)] <Insert dimensions>.

c. Water Capacity:  [268 gal. (1014 L)] <Insert amount>.

d. Material:  Stainless steel.

e. Supports:  Legs or base.

f. Controls.

g. Thermometer:  Control panel or tank rim mounted.

h. Supply:  Over-the-rim fill spout.

i. Drains:  Two waste connections.

j. Electric Turbine Ejectors:  Two; one rail mounted on each side.

k. Thermostatic, mixing-valve assembly.

l. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Add or delete optional features below to suit Project.  Many are available.

m. Hose and hand-held shower.

n. Wash-out-hose assembly.

o. Stretcher lift.

p. Overhead[ electric] hoist.

q. <Insert required option.>

Copy and edit paragraph and subparagraphs below for each type medium, Hubbard immersion tank required.

F. Medium, Hubbard Immersion Tanks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ARJO.

b. <Insert manufacturer's name.>

4. Description:  Stationary, butterfly-shaped tank, for full-body massage.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 17 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Tank Dimensions:  [100 by 73 by 24 inches (2540 by 1854 by 610 mm)] <Insert dimensions>.

b. Overall Height:  [34 to 38 inches (864 to 965 mm)] <Insert dimensions>.

c. Water Capacity:  [377 gal. (1468 L)] <Insert amount>.

d. Material:  Stainless steel.

e. Supports:  Legs or base.

f. Controls.

g. Thermometer:  Control panel or tank rim mounted.

h. Supply:  Over-the-rim fill spout.

i. Drain:  One waste connection.

j. Electric Turbine Ejector:  One, panel mounted.

k. Thermostatic, mixing-valve assembly.

l. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Add or delete optional features below to suit Project.  Many are available.

m. Hose and hand-held shower.

n. Wash-out-hose assembly.

o. Stretcher lift.

p. Overhead[ electric] hoist.

q. <Insert required option.>

Copy and edit paragraph and subparagraphs below for each type large, Hubbard immersion tank required.

G. Large, Hubbard Immersion Tanks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Ferno Ille; a div. of Ferno-Washington, Inc.

b. Whitehall Manufacturing; a division of Acorn Engineering Company.

c. <Insert manufacturer's name.>

4. Description:  Stationary, butterfly-shaped tank, for full-body massage.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 17 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Tank Dimensions:  [106 by 77 by 22 inches (2692 by 1956 by 560 mm)] <Insert dimensions>.

b. Overall Height:  [34 inches (864 mm)] <Insert dimension>.

c. Water Capacity:  [425 gal. (1609 L)] <Insert amount>.

d. Material:  Stainless steel.

e. Supports:  Legs or base.

f. Controls.

g. Thermometer:  Control panel or tank rim mounted.

h. Supply:  Over-the-rim fill spout.

i. Drain(s):  One or two waste connections.

j. Electric Turbine Ejectors:  Two; one rail mounted on each side.

k. Thermostatic, mixing-valve assembly.

l. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Add or delete optional features below to suit Project.  Many are available.

m. Hose and hand-held shower.

n. Wash-out-hose assembly.

o. Stretcher lift.

p. Overhead[ electric] hoist.

q. <Insert required option.>

Copy and edit paragraph and subparagraphs below for each type full-body immersion tank required.

H. Full-Body Immersion Tanks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ARJO.

b. Ferno Ille; a div. of Ferno-Washington, Inc.

c. Whitehall Manufacturing; a division of Acorn Engineering Company.

d. <Insert manufacturer's name.>

4. Description:  Stationary, rectangular tank, for full-body massage

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 17 subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Tank Dimensions:  [90 by 32 by 19 inches (2286 by 813 by 483 mm)] [95 by 41 by 22 inches (2413 by 1041 by 560 mm)] <Insert dimensions>.

b. Overall Height:  32 or 34 inches (813 or 860 mm).

c. Water Capacity:  [195 gal. (738 L)] [260 gal. (984 L)] <Insert amount>.

d. Material:  Stainless steel.

e. Supports:  Legs or base.

f. Controls.

g. Thermometer:  Control panel or tank rim mounted.

h. Supply:  Over-the-rim fill spout.

i. Drain(s):  One or two waste connections.

j. Electric Turbine Ejector:  One, tank mounted [at end] [on rail] [on side].

k. Thermostatic, mixing-valve assembly.

l. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

Add or delete optional features below to suit Project.  Many are available.

m. Hose and hand-held shower.

n. Wash-out-hose assembly.

o. Stretcher lift.

p. Overhead[ electric] hoist.

q. <Insert required option.>

2.22 OUTLET BOXES

Caution:  Authorities having jurisdiction may require backflow preventers in water-supply piping or on hose-thread outlets.

Copy and edit paragraph and subparagraphs in this Article for each type dialysis equipment outlet box required.

A. Dialysis Equipment Outlet Boxes, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Acorn Engineering Company.

b. Bradley Corporation.

c. Metcraft Industries Inc.

d. Whitehall Manufacturing; a division of Acorn Manufacturing Company.

e. <Insert manufacturer's name.>

4. Description:  Recessed-mounting outlet box with water supply and drain connections.

a. Box and Faceplate:  Stainless steel.

Add a subparagraph for box dimensions here if required.

b. Supply Fitting(s):  [1] [2] NPS 1/2 (DN 15) PVC ball valve(s) and adapter with male hose-thread outlet.

c. Drain:  NPS 2 (DN 50) standpipe, P-trap, and direct waste connection to drainage piping.

5. Reinforcement:  2-by-4-inch (50-by-100-mm) fire-retardant-treated-wood blocking between studs.  Fire-retardant-treated wood blocking is specified in Division 06 Section "Rough Carpentry."

2.23 MORGUE EQUIPMENT

Equipment in this Article is often custom-made.  Consult user or manufacturer's representative before equipment and option selection.

Copy and edit paragraphs and subparagraphs below for each type morgue equipment required.

A. Autopsy Tables, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Jewett.

b. Thermo Electron Corporation.

c. <Insert manufacturer's name.>

4. Description:  Pedestal stainless-steel table with sink; designed for downdraft ventilation.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 12 subparagraphs and associated subparagraphs below may be reduced, omitted, or added to.

a. Material:  Stainless steel.

b. Overall Size:  Approximately [88 by 30 inches (2250 by 760 mm)] <Insert dimensions> with deck faucet holes.

c. Faucet:  Deck mounted with wrist- or elbow-blade handles.

d. Aspirator:  Deck mounted.

e. Removable body supports.

f. Rinse Assembly:  Deck-mounted faucet with hose.

g. Disposer:  [Not required] [Required].

h. Fixture Support:  Sink <Insert designation>.

i. Receptacle:  Duplex, hospital grade with ground-fault interruption.

j. Supplies:  Chrome-plated copper tubes[ or flexible connectors] with atmospheric vacuum breakers and stops.

k. Drain:  [Chrome-plated, cast-brass P-trap and waste to wall] <Insert material and type of drain>.

l. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

B. Dissecting Sinks, <Insert drawing designation>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Jewett.

b. Thermo Electron Corporation.

c. <Insert manufacturer's name.>

4. Description:  Wall-mounting sink with backsplash.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in 13 subparagraphs and associated subparagraphs below may be reduced, omitted, or added to.

a. Material:  Stainless steel.

b. Overall Size:  [84 by 28 inches (2134 by 711 mm)] <Insert dimensions> with back faucet holes.

c. Sink Size:  Approximately 30 inches (763 mm) wide.

d. Equipment drawer.

e. Faucet:  Back mounted with wrist- or elbow-blade handles.

f. Aspirator:  Back mounted.

g. Rinse Assembly:  One back-mounted faucet with hose.

h. Disposer:  [Not required] [Required].

i. Fixture Support:  Sink <Insert designation>.

j. Supplies:  Chrome-plated copper tubes[ or flexible connectors] with atmospheric vacuum breakers and stops.

k. Drain:  [Chrome-plated, cast-brass] <Insert material> P-trap and waste to wall.

l. Back-mounted, hand-held-type eye wash.

m. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert number> V.

2) Phase(s):  [One] [Three].

3) Hertz:  [60] <Insert number> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for medical plumbing fixtures to verify actual locations of piping connections before fixture installation.

B. Examine cabinets, counters, floors, and walls for suitable conditions where fixtures will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Assemble medical plumbing fixtures, trim, fittings, and other components according to manufacturers' written instructions.

B. Install off-floor supports, affixed to building substrate, for wall-mounting fixtures.

1. Use carrier supports with waste fitting and seal for back-outlet fixtures.

2. Use carrier supports without waste fitting for fixtures with tubular waste piping.

3. Use chair-type carrier supports with rectangular steel uprights for accessible fixtures.

C. Install back-outlet, wall-mounting fixtures onto waste fitting seals and attach to supports.

D. Install floor-mounting fixtures on closet flanges or other attachments to piping or building substrate.

E. Install wall-mounting fixtures with tubular waste piping attached to supports.

F. Install counter-mounting fixtures in and attached to casework.

G. Install fixtures level and plumb according to roughing-in drawings.

H. Install water-supply piping with stop on each supply to each fixture to be connected to domestic water piping.  Attach supplies to supports or substrate within pipe spaces behind fixtures.  Install stops in locations where they can be easily reached for operation.

1. Exception:  Use ball, gate, or globe valve if stops are not specified with fixture.  Valves are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

I. Install trap and tubular waste piping on drain outlet of each fixture to be directly connected to sanitary drainage system.

J. Install flushometer valves for accessible water closets with handle mounted on wide side of compartment.  Install other actuators in locations that are easy for people with disabilities to reach.

K. Install toilet seats on water closets.

L. Install faucet-spout fittings with specified flow rates and patterns in faucet spouts if faucets are not available with required rates and patterns.  Include adapters if required.

M. Install shower flow-control fittings with specified maximum flow rates in shower arms.

N. Install traps on fixture outlets.

1. Exception:  Omit trap on fixtures with integral traps.

O. Install escutcheons at piping wall penetrations in exposed, finished locations and within cabinets and millwork.  Use deep-pattern escutcheons if required to conceal protruding fittings.  Escutcheons are specified in Division 22 Section "Common Work Results for Plumbing."

P. Set showers in leveling bed of cement grout.  Grout is specified in Division 22 Section "Common Work Results for Plumbing."

Delete paragraph below if sealants are specified in Division 07 Section "Joint Sealants."

Q. Seal joints between fixtures and walls, floors, and counters using sanitary-type, one-part, mildew-resistant silicone sealant.  Match sealant color to fixture color.  Sealants are specified in Division 07 Section "Joint Sealants."

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect water supplies from domestic water piping to medical plumbing fixtures.

C. Connect drain piping from medical plumbing fixtures to sanitary waste and vent piping.

D. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

E. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Verify that installed medical plumbing fixtures are categories and types specified for locations where installed.

B. Check that medical plumbing fixtures are complete with trim, faucets, fittings, and other specified components.

C. Inspect installed medical plumbing fixtures for damage.  Replace damaged fixtures and components.

D. Test installed fixtures after water systems are pressurized for proper operation.  Replace malfunctioning fixtures and components, then retest.  Repeat procedure until units operate properly.

E. Install fresh batteries in sensor-operated mechanisms.

3.5 ADJUSTING

A. Operate and adjust faucets and controls.  Replace damaged and malfunctioning medical plumbing fixtures, fittings, and controls.

Delete fixture types in first paragraph below not in Project.

B. Adjust water pressure at [faucets] [shower valves] [and] [flushometer valves] to produce proper flow and stream.

C. Replace washers and seals of leaking and dripping faucets and stops.

3.6 CLEANING

A. Clean medical plumbing fixtures, faucets, and other fittings with manufacturers' recommended cleaning methods and materials.  Do the following:

1. Remove faucet spouts and strainers, remove sediment and debris, and reinstall strainers and spouts.

2. Remove sediment and debris from drains.

B. After completing installation of exposed, factory-finished fixtures, faucets, and fittings, inspect exposed finishes and repair damaged finishes.

3.7 PROTECTION

A. Provide protective covering for installed fixtures and fittings.

B. Do not allow use of medical plumbing fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224300

HEALTHCARE PLUMBING FIXTURES
224300 - 1

