Copyright 2005 AIA
MASTERSPEC Full Length
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Equipment labels.

2. Warning signs and labels.

3. Pipe labels.

4. Duct labels.

5. Stencils.

6. Valve tags.

7. Warning tags.

1.3 SUBMITTALS

Submittals in this article are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.

B. Samples:  For color, letter style, and graphic representation required for each identification material and device.

C. Equipment Label Schedule:  Include a listing of all equipment to be labeled with the proposed content for each label.

D. Valve numbering scheme.

E. Valve Schedules:  For each piping system to include in maintenance manuals.

1.4 COORDINATION

A. Coordinate installation of identifying devices with completion of covering and painting of surfaces where devices are to be applied.

B. Coordinate installation of identifying devices with locations of access panels and doors.

C. Install identifying devices before installing acoustical ceilings and similar concealment.

PART 2 -  PRODUCTS

2.1 EQUIPMENT LABELS

A. Metal Labels for Equipment:

Retain and punctuate multiple material options in first subparagraph below to allow Contractor to select most cost-effective material.

1. Material and Thickness:  [Brass, 0.032-inch (0.8-mm)] [Stainless steel, 0.025-inch (0.64-mm)] [Aluminum, 0.032-inch (0.8-mm)] [or] [anodized aluminum, 0.032-inch (0.8-mm)] minimum thickness, and having predrilled or stamped holes for attachment hardware.

2. Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

3. Minimum Letter Size:  1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

4. Fasteners:  Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

5. Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

B. Plastic Labels for Equipment:

1. Material and Thickness:  Multilayer, multicolor, plastic labels for mechanical engraving, [1/16 inch (1.6 mm)] [1/8 inch (3.2 mm)] <Insert dimension> thick, and having predrilled holes for attachment hardware.

2. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

3. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

4. Maximum Temperature:  Able to withstand temperatures up to 160 deg F (71 deg C).

5. Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

6. Minimum Letter Size:  1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

7. Fasteners:  Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

8. Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

In first paragraph below, describe required label content.  The objective of labeling equipment is to coordinate it with Drawings, including plans, details, and schedules.  This will allow other information, such as capacities and operating characteristics, to be obtained.

C. Label Content:  Include equipment's Drawing designation or unique equipment number, Drawing numbers where equipment is indicated (plans, details, and schedules), plus the Specification Section number and title where equipment is specified.

D. Equipment Label Schedule:  For each item of equipment to be labeled, on 8-1/2-by-11-inch (A4) bond paper.  Tabulate equipment identification number and identify Drawing numbers where equipment is indicated (plans, details, and schedules), plus the Specification Section number and title where equipment is specified.  Equipment schedule shall be included in operation and maintenance data.

2.2 WARNING SIGNS AND LABELS

A. Material and Thickness:  Multilayer, multicolor, plastic labels for mechanical engraving, [1/16 inch (1.6 mm)] [1/8 inch (3.2 mm)] <Insert dimension> thick, and having predrilled holes for attachment hardware.

B. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

C. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

D. Maximum Temperature:  Able to withstand temperatures up to 160 deg F (71 deg C).

E. Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

F. Minimum Letter Size:  1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

G. Fasteners:  Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

H. Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

In paragraph below, describe required label content.  The objective of labeling equipment is to coordinate it with Drawings, including plans, details, and schedules.  This will allow other information, such as capacities and operating characteristics, to be obtained.

I. Label Content:  Include caution and warning information, plus emergency notification instructions.

2.3 PIPE LABELS

Retain this article if these devices will identify some or all piping.  Identification of piping by color-coded painting is covered in "Pipe Label Installation" Article.

Do not use pipe labels or plastic tapes for bare pipes conveying fluids at temperatures of 125 deg F (52 deg C) or higher.

A. General Requirements for Manufactured Pipe Labels:  Preprinted, color-coded, with lettering indicating service, and showing flow direction.

B. Pretensioned Pipe Labels:  Precoiled, semirigid plastic formed to [partially cover] [cover full] circumference of pipe and to attach to pipe without fasteners or adhesive.

C. Self-Adhesive Pipe Labels:  Printed plastic with contact-type, permanent-adhesive backing.

D. Pipe Label Contents:  Include identification of piping service using same designations or abbreviations as used on Drawings, pipe size, and an arrow indicating flow direction.

1. Flow-Direction Arrows:  Integral with piping system service lettering to accommodate both directions, or as separate unit on each pipe label to indicate flow direction.

2. Lettering Size:  At least 1-1/2 inches (38 mm) high.

2.4 DUCT LABELS

A. Material and Thickness:  Multilayer, multicolor, plastic labels for mechanical engraving, [1/16 inch (1.6 mm)] [1/8 inch (3.2 mm)] <Insert dimension> thick, and having predrilled holes for attachment hardware.

B. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

C. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

D. Maximum Temperature:  Able to withstand temperatures up to 160 deg F (71 deg C).

E. Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

F. Minimum Letter Size:  1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

G. Fasteners:  Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

H. Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

I. Duct Label Contents:  Include identification of duct service using same designations or abbreviations as used on Drawings, duct size, and an arrow indicating flow direction.

1. Flow-Direction Arrows:  Integral with duct system service lettering to accommodate both directions, or as separate unit on each duct label to indicate flow direction.

2. Lettering Size:  At least 1-1/2 inches (38 mm) high.

2.5 STENCILS

A. Stencils:  Prepared with letter sizes according to ASME A13.1 for piping; minimum letter height of 1-1/4 inches (32 mm) for ducts; and minimum letter height of 3/4 inch (19 mm) for access panel and door labels, equipment labels, and similar operational instructions.

1. Stencil Material:  [Aluminum] [Brass] [Fiberboard] [Fiberboard or metal] <Insert material>.

2. Stencil Paint:  Exterior, gloss, [alkyd enamel] [acrylic enamel] <Insert paint type> black unless otherwise indicated.  Paint may be in pressurized spray-can form.

3. Identification Paint:  Exterior, [alkyd enamel] [acrylic enamel] <Insert paint type> in colors according to ASME A13.1 unless otherwise indicated.

2.6 VALVE TAGS

Retain requirement in "Submittals" Article to submit numbering scheme for approval.

A. Valve Tags:  Stamped or engraved with 1/4-inch (6.4-mm) letters for piping system abbreviation and 1/2-inch (13-mm) numbers.

1. Tag Material:  [Brass, 0.032-inch (0.8-mm)] [Stainless steel, 0.025-inch (0.64-mm)] [Aluminum, 0.032-inch (0.8-mm)] [or] [anodized aluminum, 0.032-inch (0.8-mm)] minimum thickness, and having predrilled or stamped holes for attachment hardware.

2. Fasteners:  Brass [wire-link or beaded chain; or S-hook] [wire-link chain] [beaded chain] [S-hook].

B. Valve Schedules:  For each piping system, on 8-1/2-by-11-inch (A4) bond paper.  Tabulate valve number, piping system, system abbreviation (as shown on valve tag), location of valve (room or space), normal-operating position (open, closed, or modulating), and variations for identification.  Mark valves for emergency shutoff and similar special uses.

1. Valve-tag schedule shall be included in operation and maintenance data.

2.7 WARNING TAGS

A. Warning Tags:  Preprinted or partially preprinted, accident-prevention tags, of plasticized card stock with matte finish suitable for writing.

1. Size:  [3 by 5-1/4 inches (75 by 133 mm) minimum] [Approximately 4 by 7 inches (100 by 178 mm)] <Insert size>.

2. Fasteners:  [Brass grommet and wire] [Reinforced grommet and wire or string].

3. Nomenclature:  Large-size primary caption such as "DANGER," "CAUTION," or "DO NOT OPERATE."

4. Color:  Yellow background with black lettering.

PART 3 -  EXECUTION

3.1 PREPARATION

A. Clean piping and equipment surfaces of substances that could impair bond of identification devices, including dirt, oil, grease, release agents, and incompatible primers, paints, and encapsulants.

3.2 EQUIPMENT LABEL INSTALLATION

A. Install or permanently fasten labels on each major item of mechanical equipment.

B. Locate equipment labels where accessible and visible.

3.3 PIPE LABEL INSTALLATION

Retain first paragraph below to identify piping systems by color-coded painting.  Labels will still be required to identify service, pipe size, and flow direction.

A. Piping Color-Coding:  Painting of piping is specified in Division 09 Section "[Interior Painting] [High-Performance Coatings]."

Retain first paragraph below only if stenciled labels are permitted.

B. Stenciled Pipe Label Option:  Stenciled labels may be provided instead of manufactured pipe labels, at Installer's option.  Install stenciled pipe labels [with painted, color-coded bands or rectangles] [, complying with ASME A13.1,] on each piping system.

1. Identification Paint:  Use for contrasting background.

2. Stencil Paint:  Use for pipe marking.

Revise first paragraph below to suit Project.

C. Locate pipe labels where piping is exposed or above accessible ceilings in finished spaces; machine rooms; accessible maintenance spaces such as shafts, tunnels, and plenums; and exterior exposed locations as follows:

1. Near each valve and control device.

2. Near each branch connection, excluding short takeoffs for fixtures and terminal units.  Where flow pattern is not obvious, mark each pipe at branch.

3. Near penetrations through walls, floors, ceilings, and inaccessible enclosures.

4. At access doors, manholes, and similar access points that permit view of concealed piping.

5. Near major equipment items and other points of origination and termination.

6. Spaced at maximum intervals of [50 feet (15 m)] <Insert dimension> along each run.  Reduce intervals to [25 feet (7.6 m)] <Insert dimension> in areas of congested piping and equipment.

7. On piping above removable acoustical ceilings.  Omit intermediately spaced labels.

D. Pipe Label Color Schedule:

1. Chilled-Water Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

2. Condenser-Water Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

3. Heating Water Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

4. Refrigerant Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

5. Low-Pressure Steam Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

6. High-Pressure Steam Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

7. Steam Condensate Piping:

a. Background Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color:  [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

3.4 DUCT LABEL INSTALLATION

A. Install [plastic-laminated] [self-adhesive] duct labels with permanent adhesive on air ducts in the following color codes:

1. [Blue] <Insert color>:  For cold-air supply ducts.

2. [Yellow] <Insert color>:  For hot-air supply ducts.

3. [Green] <Insert color>:  For exhaust-, outside-, relief-, return-, and mixed-air ducts.

4. ASME A13.1 Colors and Designs:  For hazardous material exhaust.

Retain first paragraph below only if stenciled labels are permitted.

B. Stenciled Duct Label Option:  Stenciled labels, showing service and flow direction, may be provided instead of plastic-laminated duct labels, at Installer's option, if lettering larger than 1 inch (25 mm) high is needed for proper identification because of distance from normal location of required identification.

C. Locate labels near points where ducts enter into concealed spaces and at maximum intervals of [50 feet (15 m)] <Insert dimension> in each space where ducts are exposed or concealed by removable ceiling system.

3.5 VALVE-TAG INSTALLATION

Revise this article as required to delete an entire piping system from tagging or other changes.  A schedule is helpful for complex projects.  Retain and revise first paragraph below if a schedule is prepared.

A. Install tags on valves and control devices in piping systems, except check valves; valves within factory-fabricated equipment units; shutoff valves; faucets; convenience and lawn-watering hose connections; and HVAC terminal devices and similar roughing-in connections of end-use fixtures and units.  List tagged valves in a valve schedule.

B. Valve-Tag Application Schedule:  Tag valves according to size, shape, and color scheme and with captions similar to those indicated in the following subparagraphs:

Other valve-tag sizes, shapes, colors, and letter colors may be available if required.

1. Valve-Tag Size and Shape:

a. Chilled Water:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

b. Condenser Water:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

c. Refrigerant:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

d. Hot Water:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

e. Gas:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

f. Low-Pressure Steam:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

g. High-Pressure Steam:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

h. Steam Condensate:  [1-1/2 inches (38 mm)] [2 inches (50 mm)], [round] [square] <Insert shape>.

Select contrasting valve-tag color and letter color in two subparagraphs below for each service.  Retain "Natural" option for brass or stainless-steel valve tags.

2. Valve-Tag Color:

a. Chilled Water:  [Natural] [Green] <Insert color>.

b. Condenser Water:  [Natural] [Green] <Insert color>.

c. Refrigerant:  [Natural] [Green] <Insert color>.

d. Hot Water:  [Natural] [Green] <Insert color>.

e. Gas:  [Natural] [Yellow] <Insert color>.

f. Low-Pressure Steam:  [Natural] [Yellow] <Insert color>.

g. High-Pressure Steam:  [Natural] [Green] <Insert color>.

h. Steam Condensate:  [Natural] [Green] <Insert color>.

3. Letter Color:

a. Chilled Water:  [Black] [White] <Insert color>.

b. Condenser Water:  [Black] [White] <Insert color>.

c. Refrigerant:  [Black] [White] <Insert color>.

d. Hot Water:  [Black] [White] <Insert color>.

e. Gas:  [Black] [White] <Insert color>.

f. Low-Pressure Steam:  [Black] [White] <Insert color>.

g. High-Pressure Steam:  [Black] [White] <Insert color>.

h. Steam Condensate:  [Black] [White] <Insert color>.

3.6 WARNING-TAG INSTALLATION

A. Write required message on, and attach warning tags to, equipment and other items where required.

END OF SECTION 230553

	IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT
	230553 - 1



