Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
06/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232213 - STEAM AND CONDENSATE HEATING PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following for [LP] [LP and HP] [HP] steam and condensate piping:

1. Pipe and fittings.

2. Strainers.

3. Flash tanks.

4. Safety valves.

5. Pressure-reducing valves.

6. Steam traps.

7. Thermostatic air vents and vacuum breakers.

8. Steam and condensate meters.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. HP Systems:  High-pressure piping operating at more than 15 psig (104 kPa) as required by ASME B31.1.

B. LP Systems:  Low-pressure piping operating at 15 psig (104 kPa) or less as required by ASME B31.9.

RTRF and RTRP in two paragraphs below are ASTM abbreviations.

C. RTRF:  Reinforced thermosetting resin (fiberglass) fittings.

D. RTRP:  Reinforced thermosetting resin (fiberglass) pipe.

1.4 PERFORMANCE REQUIREMENTS

A. Components and installation shall be capable of withstanding the following minimum working pressures and temperatures:

Insert minimum working pressure for systems in first two subparagraphs below.

1. HP Steam Piping:  <Insert psig (kPa).>

2. LP Steam Piping:  <Insert psig (kPa).>

Insert or select minimum working pressure and temperature for systems in first two subparagraphs below.

3. Condensate Piping:  <Insert psig (kPa)> at [250 deg F (121 deg C)] <Insert temperature>.

4. Makeup-Water Piping:  [80 psig (552 kPa)] <Insert pressure> at [150 deg F (66 deg C)] <Insert temperature>.

5. Blowdown-Drain Piping:  Equal to pressure of the piping system to which it is attached.

6. Air-Vent and Vacuum-Breaker Piping:  Equal to pressure of the piping system to which it is attached.

7. Safety-Valve-Inlet and -Outlet Piping:  Equal to pressure of the piping system to which it is attached.

1.5 SUBMITTALS

A. Product Data:  For each type of the following:

1. RTRP and RTRF with adhesive.

2. Pressure-reducing and safety valve.

3. Steam trap.

4. Air vent and vacuum breaker.

5. Flash tank.

6. Meter.

B. Shop Drawings:  Detail, [1/4 inch equals 1 foot (1:50)] <Insert value> scale, flash tank assemblies and fabrication of pipe anchors, hangers, pipe, multiple pipes, alignment guides, and expansion joints and loops and their attachment to the building structure.  Detail locations of anchors, alignment guides, and expansion joints and loops.

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For Installer.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For valves, safety valves, pressure-reducing valves, steam traps, air vents, vacuum breakers, and meters to include in emergency, operation, and maintenance manuals.

1.6 QUALITY ASSURANCE

A. Installer Qualifications:

Retain subparagraph below for fiberglass pipe assembly.

1. Fiberglass Pipe and Fitting Installers:  Installers of RTRF and RTRP shall be certified by the manufacturer of pipes and fittings as having been trained and qualified to join fiberglass piping with manufacturer-recommended adhesive.

Retain two paragraphs and associated subparagraphs below for welded supports or piping.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

B. Steel Support Welding:  Qualify processes and operators according to AWS D1.1, "Structural Welding Code - Steel."

C. Pipe Welding:  Qualify processes and operators according to the following:

1. Comply with provisions in ASME B31 Series, "Code for Pressure Piping."

2. Certify that each welder has passed AWS qualification tests for welding processes involved and that certification is current.

Retain applicable options in paragraph below.  Retain all three options if steam system includes high and low pressure.

D. ASME Compliance:  Comply with [ASME B31.1, "Power Piping" ] [and] [ASME B31.9, "Building Services Piping" ] for materials, products, and installation.  Safety valves and pressure vessels shall bear the appropriate ASME label.  Fabricate and stamp flash tanks to comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

PART 2 -  PRODUCTS

First three articles below include examples of materials listed in the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment," Chapter 41, "Pipes, Tubes, and Fittings."  See "Writing Guide" Article in the Evaluations for discussion of this Section's organization and of the most efficient way to edit this Section.

2.1 COPPER TUBE AND FITTINGS

A. Drawn-Temper Copper Tubing:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M, Type C)].

B. Annealed-Temper Copper Tubing:  ASTM B 88, Type K (ASTM B 88M, Type A).

C. Wrought-Copper Fittings and Unions:  ASME B16.22.

2.2 STEEL PIPE AND FITTINGS

A. Steel Pipe:  ASTM A 53/A 53M, black steel, plain ends, Type, Grade, and Schedule as indicated in Part 3 piping applications articles.

Coordinate flange class in first four paragraphs below with products in other parts of this Section and in related Sections to match face size and bolt patterns.

B. Cast-Iron Threaded Fittings:  ASME B16.4; Classes 125, 150, and 300 as indicated in Part 3 piping applications articles.

C. Malleable-Iron Threaded Fittings:  ASME B16.3; Classes 150 and 300 as indicated in Part 3 piping applications articles.

D. Malleable-Iron Unions:  ASME B16.39; Classes 150, 250, and 300 as indicated in Part 3 piping applications articles.

E. Cast-Iron Threaded Flanges and Flanged Fittings:  ASME B16.1, Classes 125 and 250 as indicated in Part 3 piping applications articles; raised ground face, and bolt holes spot faced.

F. Wrought-Steel Fittings:  ASTM A 234/A 234M, wall thickness to match adjoining pipe.

Flanges and fittings in first paragraph and subparagraphs below are available in several classes, materials, facings, and end connections.

G. Wrought-Steel Flanges and Flanged Fittings:  ASME B16.5, including bolts, nuts, and gaskets of the following material group, end connections, and facings:

1. Material Group:  1.1.

2. End Connections:  Butt welding.

3. Facings:  Raised face.

H. Steel Pipe Nipples:  ASTM A 733, made of ASTM A 53/A 53M, black steel of same Type, Grade, and Schedule as pipe in which installed.

I. Stainless-Steel Bellows, Flexible Connectors:

1. Body:  Stainless-steel bellows with woven, flexible, bronze, wire-reinforced, protective jacket.

2. End Connections:  Threaded or flanged to match equipment connected.

3. Performance:  Capable of 3/4-inch (20-mm) misalignment.

4. CWP Rating:  150-psig (1035-kPa).

5. Maximum Operating Temperature:  250 deg F (121 deg C).

2.3 FIBERGLASS PIPE AND FITTINGS

Piping is available with ends for other types of joints.  See the Evaluations for discussion of product characteristics and maximum temperatures and pressures.

A. RTRP:  ASTM D 2996 filament-wound pipe with tapered bell and spigot ends for adhesive joints.

B. RTRF:  Compression or spray-up/contact molded fittings of same material, pressure class, and joining method as pipe.

C. Flanges:  ASTM D 4024 full-face gaskets suitable for the service, minimum 1/8 inch (3.2 mm) thick, 60-70 durometer.  ASTM A 307, Grade B, hex head bolts with washers.

D. Bonding Adhesive for Fiberglass Piping:  As recommended by fiberglass piping manufacturer.

2.4 JOINING MATERIALS

A. Pipe-Flange Gasket Materials:  Suitable for chemical and thermal conditions of piping system contents.

1. ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

a. Full-Face Type:  For flat-face, Class 125, cast-iron and cast-bronze flanges.

b. Narrow-Face Type:  For raised-face, Class 250, cast-iron and steel flanges.

B. Flange Bolts and Nuts:  ASME B18.2.1, carbon steel, unless otherwise indicated.

C. Solder Filler Metals:  ASTM B 32, lead-free alloys.  Include water-flushable flux according to ASTM B 813.

D. Brazing Filler Metals:  AWS A5.8, BCuP Series, copper-phosphorus alloys for joining copper with copper; or BAg-1, silver alloy for joining copper with bronze or steel.

E. Welding Filler Metals:  Comply with AWS D10.12 (AWS D10.12M) for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

F. Welding Materials:  Comply with Section II, Part C, of ASME Boiler and Pressure Vessel Code for welding materials appropriate for wall thickness and for chemical analysis of pipe being welded.

2.5 DIELECTRIC FITTINGS

A. Description:  Combination fitting of copper alloy and ferrous materials with threaded, solder-joint, plain, or weld-neck end connections that match piping system materials.

B. Insulating Material:  Suitable for system fluid, pressure, and temperature.

Revise pressure ratings and temperatures in three paragraphs and associated subparagraphs below to suit Project or add other options for specific applications.

C. Dielectric Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. Hart Industries, International Inc.

d. Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group.

f. <Insert manufacturer's name.>

3. Factory-fabricated union assembly, for 250-psig (1725-kPa) minimum working pressure at 180 deg F (82 deg C).

D. Dielectric Flanges:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. Watts Water Technologies, Inc..

d. <Insert manufacturer's name.>

3. Factory-fabricated companion-flange assembly, for 150- or 300-psig (1035- or 2070-kPa) minimum working pressure as required to suit system pressures.

E. Dielectric-Flange Kits:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Advance Products & Systems, Inc.

b. Calpico, Inc.

c. Central Plastics Company.

d. Pipeline Seal and Insulator, Inc.

e. <Insert manufacturer's name.>

3. Companion-flange assembly for field assembly.  Include flanges, full-face- or ring-type neoprene or phenolic gasket, phenolic or polyethylene bolt sleeves, phenolic washers, and steel backing washers.

4. Separate companion flanges and steel bolts and nuts shall have 150- or 300-psig (1035- or 2070-kPa) minimum working pressure as required to suit system pressures.

2.6 VALVES

A. Gate, Globe, Check, Ball, and Butterfly Valves:  Comply with requirements specified in Division 23 Section "General-Duty Valves for HVAC Piping."

B. Stop-Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Crane Co.

b. Jenkins Valves; a Crane Company.

c. Lunkenheimer Valves.

d. A.Y. McDonald Mfg. Co.

e. <Insert manufacturer's name.>

4. Body and Bonnet:  Malleable iron.

5. End Connections:  Flanged.

6. Disc:  Cylindrical with removable liner and machined seat.

7. Stem:  Brass alloy.

8. Operator:  Outside screw and yoke with cast-iron handwheel.

9. Packing:  Polytetrafluoroethylene-impregnated packing with two-piece packing gland assembly.

10. Pressure Class:  250.

2.7 STRAINERS

A. Y-Pattern Strainers:

1. Body:  ASTM A 126, Class B cast iron, with bolted cover and bottom drain connection.

2. End Connections:  Threaded ends for strainers NPS 2 (DN 50) and smaller; flanged ends for strainers NPS 2-1/2 (DN 65) and larger.

3. Strainer Screen:  Stainless-steel, [20] <Insert size> mesh strainer, and perforated stainless-steel basket with 50 percent free area.

4. Tapped blowoff plug.

5. CWP Rating:  250-psig (1725-kPa) working steam pressure.

B. Basket Strainers:

1. Body:  ASTM A 126, Class B cast iron, with bolted cover and bottom drain connection.

2. End Connections:  Threaded ends for strainers NPS 2 (DN 50) and smaller; flanged ends for strainers NPS 2-1/2 (DN 65) and larger.

3. Strainer Screen:  Stainless-steel, [20] <Insert size> mesh strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating:  250-psig (1725-kPa) working steam pressure.

2.8 FLASH TANKS

A. Shop or factory fabricated of welded steel according to ASME Boiler and Pressure Vessel Code, for 150-psig (1035-kPa) rating; and bearing ASME label.  Fabricate with tappings for low-pressure steam and condensate outlets, high-pressure condensate inlet, air vent, safety valve, and legs.

2.9 SAFETY VALVES

Valves in paragraph and subparagraphs below are available in NPS 1/2 through NPS 2-1/2 (DN 15 through DN 65).

A. [Bronze] [or] [Brass] Safety Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Kunkle Valve; a Tyco International Ltd. Company.

c. Spirax Sarco, Inc.

d. Watts Water Technologies, Inc.

e. <Insert manufacturer's name.>

4. Disc Material:  Forged copper alloy.

5. End Connections:  Threaded inlet and outlet.

6. Spring:  Fully enclosed steel spring with adjustable pressure range and positive shutoff, factory set and sealed.

7. Pressure Class:  250.

8. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

9. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code.

Valves in paragraph and subparagraphs below are available in NPS 1-1/2 through NPS 6 (DN 40 through DN 150).

B. Cast-Iron Safety Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Kunkle Valve; a Tyco International Ltd. Company.

c. Spirax Sarco, Inc.

d. Watts Water Technologies, Inc.

e. <Insert manufacturer's name.>

4. Disc Material:  Forged copper alloy with bronze nozzle.

5. End Connections:  Raised-face flanged inlet and threaded or flanged outlet connections.

6. Spring:  Fully enclosed cadmium-plated steel spring with adjustable pressure range and positive shutoff, factory set and sealed.

7. Pressure Class:  250.

8. Drip-Pan Elbow:  Cast iron and having threaded inlet, outlet, and drain, with threads complying with ASME B1.20.1.

9. Exhaust Head:  Cast iron and having threaded inlet and drain, with threads complying with ASME B1.20.1.

10. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code.

2.10 PRESSURE-REDUCING VALVES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Armstrong International, Inc.

2. Hoffman Specialty; Division of ITT Industries.

3. Leslie Controls, Inc.

4. Spence Engineering Company, Inc.

5. Spirax Sarco, Inc.

6. <Insert manufacturer's name.>

Schedule pressure-reducing valves and include size, capacity, minimum length of straight pipe on both sides of valve, and inlet and outlet pressures.  Select pressure-reducing valves to develop no more than 85 dBA at an elevation of 3 feet (1 m) above adjacent floor and at 3 feet (1 m) in any direction.  Use Schedule 80 minimum for piping inlet and outlet connections to pressure-reducing valves, to achieve the required sound level, or use sound attenuators.

D. Size, Capacity, and Pressure Rating:  Factory set for inlet and outlet pressures indicated.

E. Description:  Pilot-actuated, diaphragm type, with adjustable pressure range and positive shutoff.

F. Body:  Cast iron.

G. End Connections:  Threaded connections for valves NPS 2 (DN 50) and smaller and flanged connections for valves NPS 2-1/2 (DN 65) and larger.

H. Trim:  Hardened stainless steel.

I. Head and Seat:  Replaceable, main head stem guide fitted with flushing and pressure-arresting device cover over pilot diaphragm.

J. Gaskets:  Non-asbestos materials.

If Project has more than one type or size of pressure-reducing valve, delete paragraph and subparagraphs below and schedule pressure-reducing valve performance on Drawings.

K. Capacities and Characteristics:

1. Steam Flow Rate:  <Insert lb/h (kg/s).>

2. Inlet Pressure:  <Insert psig (kPa).>

3. Outlet Set Pressure:  <Insert psig (kPa).>

4. Pressure Loss (Wide Open):  <Insert psig (kPa).>

2.11 STEAM TRAPS

A. Thermostatic Traps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Barnes & Jones, Inc.

c. Dunham-Bush, Inc.

d. Hoffman Specialty; Division of ITT Industries.

e. Spirax Sarco, Inc.

f. Sterling.

g. <Insert manufacturer's name.>

4. Body:  Bronze angle-pattern body with integral union tailpiece and screw-in cap.

5. Trap Type:  Balanced-pressure.

6. Bellows:  Stainless steel or monel.

7. Head and Seat:  Replaceable, hardened stainless steel.

8. Pressure Class:  125.

B. Thermodynamic Traps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Barnes & Jones, Inc.

c. Dunham-Bush, Inc.

d. Hoffman Specialty; Division of ITT Industries.

e. Spirax Sarco, Inc.

f. <Insert manufacturer's name.>

4. Body:  Stainless steel with screw-in cap.

5. End Connections:  Threaded.

6. Disc and Seat:  Stainless steel.

7. Maximum Operating Pressure:  600 psig (4140 kPa).

C. Float and Thermostatic Traps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Barnes & Jones, Inc.

c. Dunham-Bush, Inc.

d. Hoffman Specialty; Division of ITT Industries.

e. Spirax Sarco, Inc.

f. Sterling.

g. <Insert manufacturer's name.>

4. Body and Bolted Cap:  ASTM A 126, cast iron.

5. End Connections:  Threaded.

6. Float Mechanism:  Replaceable, stainless steel.

7. Head and Seat:  Hardened stainless steel.

8. Trap Type:  Balanced pressure.

9. Thermostatic Bellows:  Stainless steel or monel.

10. Thermostatic air vent capable of withstanding 45 deg F (25 deg C) of superheat and resisting water hammer without sustaining damage.

Retain first subparagraph below for optional vacuum breaker.

11. Vacuum Breaker:  Thermostatic with phosphor bronze bellows, and stainless steel cage, valve, and seat.

12. Maximum Operating Pressure:  125 psig (860 kPa).

D. Inverted Bucket Traps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Barnes & Jones, Inc.

c. Dunham-Bush, Inc.

d. Hoffman Specialty; Division of ITT Industries.

e. Spirax Sarco, Inc.

f. Sterling.

g. <Insert manufacturer's name.>

4. Body and Cap:  Cast iron.

5. End Connections:  Threaded.

6. Head and Seat:  Stainless steel.

7. Valve Retainer, Lever, and Guide Pin Assembly:  Stainless steel.

8. Bucket:  Brass or stainless steel.

First two subparagraphs below are optional features for inverted bucket traps.

9. Strainer:  Integral stainless-steel inlet strainer within the trap body.

10. Air Vent:  Stainless-steel thermostatic vent.

11. Pressure Rating:  250 psig (1725 kPa).

2.12 THERMOSTATIC AIR VENTS AND VACUUM BREAKERS

A. Thermostatic Air Vents:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Barnes & Jones, Inc.

c. Dunham-Bush, Inc.

d. Hoffman Specialty; Division of ITT Industries.

e. Spirax Sarco, Inc.

f. Sterling.

g. <Insert manufacturer's name.>

4. Body:  Cast iron, bronze or stainless steel.

5. End Connections:  Threaded.

6. Float, Valve, and Seat:  Stainless steel.

7. Thermostatic Element:  Phosphor bronze bellows in a stainless-steel cage.

8. Pressure Rating:  [125 psig (861 kPa)] [300 psig (2068 kPa)] <Insert pressure>.

9. Maximum Temperature Rating:  [350 deg F (177 deg C)] <Insert temperature>.

B. Vacuum Breakers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armstrong International, Inc.

b. Dunham-Bush, Inc.

c. Hoffman Specialty; Division of ITT Industries.

d. Johnson Corporation (The).

e. Spirax Sarco, Inc.

f. <Insert manufacturer's name.>

4. Body:  Cast iron, bronze, or stainless steel.

5. End Connections:  Threaded.

6. Sealing Ball, Retainer, Spring, and Screen:  Stainless steel.

7. O-ring Seal:  EPR.

8. Pressure Rating:  [125 psig (861 kPa)] [300 psig (2068 kPa)] <Insert pressure>.

9. Maximum Temperature Rating:  [350 deg F (177 deg C)] <Insert temperature>.

2.13 STEAM METERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. EMCO Flow Systems; Division of Advanced Energy Company.

2. ISTEC Corp.

3. Preso Meters; a division of Racine Federated Inc.

4. Spirax Sarco, Inc.

5. <Insert manufacturer's name.>

D. Meters shall have a microprocessor to display totalizer flow, flow rate, temperature, pressure, time, and date; alarms for high and low flow rate and temperature.

1. Computer shall have 4 to 20-mA or 2 to 10 volt output for temperature, pressure, and contact closure for flow increments.

2. Independent timers to store four peak flow rates and total flow.

3. Interface compatible with central workstation described in Division 23 Section "Instrumentation and Control for HVAC."

4. Microprocessor Enclosure:  NEMA 250, Type 4.

Retain one of three paragraphs below.

E. Sensor:  Venturi, of [stainless-steel] [carbon-steel] construction, for insertion in pipeline between flanges.  At least 10:1 turndown with plus or minus 1 percent accuracy over full-flow range.

F. Sensor:  Vortex type with stainless-steel wetted parts and [wafer] [flange] connections; and with a piezoelectric sensor removable and serviceable without shutting down the process.  At least 10:1 turndown with plus or minus 1 percent accuracy over full-flow range.

G. Sensor:  Spring-loaded, variable-area flowmeter type; density compensated with stainless-steel wetted parts and [wafer] [flange] connections.  At least 10:1 turndown with plus or minus 2 percent accuracy over full-flow range.

2.14 CONDENSATE METERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Central Station Steam Co.

2. Lincoln Meter Company.

3. <Insert manufacturer's name.>

D. Body:  Cast iron, bronze, or brass.

E. Turbine:  Copper, brass, or stainless steel.

F. Connections:  Threaded for NPS 2 (DN 50) and smaller and flanged for NPS 2-1/2 (DN 65).

G. Totalizer:  Meters shall have a microprocessor to display flow, flow rate, time, and date; alarms for high and low flow rate, pressure, and temperature.

1. Computer shall have 4- to 20-mA or 2- to 10-volt output for temperature, pressure, and contact closure for flow increments.

2. Independent timers to store four peak flow rates and total flow.

3. Interface compatible with central workstation specified in Division 23 Section "Instrumentation and Control for HVAC."

4. Microprocessor Enclosure:  NEMA 250, Type 4.

H. Pressure Rating:  [Atmospheric] <Insert pressure>.

I. Maximum Temperature Rating:  [250 deg F (121 deg C)] <Insert temperature>.

PART 3 -  EXECUTION

3.1 LP STEAM PIPING APPLICATIONS

Retain at least one pipe material in paragraphs below for each service required for Project.  Services are specified separately to allow different pipe materials and joining methods for each.  If materials and methods are the same for multiple services, combine the requirements by editing the paragraph titles.  To allow the Contractor to choose among various pipe materials, retain multiple materials for each required service.  The change point for pipe materials and joining methods is specified, in this master, where the pipe size changes from NPS 2 to NPS 2-1/2 (DN 50 to DN 65).  Adjust this change point to suit office policy.  See "Writing Guide" Article in the Evaluations.

If Project includes steam and condensate piping with pressure ranges both higher and lower than 15 psig (104 kPa), retain this Article and the following "HP Steam Piping Applications" Article and identify the pressure range of steam piping on Drawings; use similar designations.  If pressure range for systems on Project is limited to 15 psig (104 kPa) and lower, or is limited to higher than 15 psig (104 kPa), retain only the appropriate Article and omit pressure designations on Drawings.  See "Writing Guide" Article in the Evaluations for discussion of the most efficient way to edit this Section.

A. LP Steam Piping, [NPS 2 (DN 50) and Smaller] <Insert pipe size range>:  Schedule [40] [80], Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

B. LP Steam Piping, [NPS 2-1/2 through NPS 12 (DN 65 through DN 300)] <Insert pipe size range>:  Schedule [40] [80], Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

C. LP Steam Piping, [NPS 14 through NPS 18 (DN 350 through DN 450)] <Insert pipe size range>:  Schedule 30, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

D. LP Steam Piping, [NPS 20 (DN 500) and Larger] <Insert pipe size range>:  Schedule 20, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

E. Condensate piping above grade, [NPS 2 (DN 50)] <Insert pipe size range> and smaller, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in first paragraph below to allow Contractor to select piping materials from those retained.

F. Condensate piping above grade, [NPS 2-1/2 (DN 65)] <Insert pipe size range> and larger, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

2. RTRP and RTRF with adhesive or flanged joints.

G. Condensate piping below grade, [NPS 2 (DN 50)] <Insert pipe size range> and smaller, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

H. Condensate piping below grade, [NPS 2-1/2 (DN 65)] <Insert pipe size range> and larger, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

2. RTRP and RTRF with adhesive or flanged joints.

3.2 HP STEAM PIPING APPLICATIONS

A. HP Steam Piping, [NPS 2 (DN 50) and Smaller] <Insert pipe size range>:  Schedule [40] [80], Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

B. HP Steam Piping, [NPS 2-1/2 through NPS 12 (DN 65 through DN 300)] <Insert pipe size range>:  Schedule [40] [80], Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

C. HP Steam Piping, [NPS 14 through NPS 18 (DN 350 through DN 450)] <Insert pipe size range>:  Schedule 30, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

D. HP Steam Piping, [NPS 20 (DN 500) and Larger] <Insert pipe size range>:  Schedule 20, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

E. Condensate piping above grade, [NPS 2 (DN 50)] <Insert pipe size range> and smaller, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in first paragraph below to allow Contractor to select piping materials from those retained.

F. Condensate piping above grade, [NPS 2-1/2 (DN 65)] <Insert pipe size range> and larger, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

2. RTRP and RTRF with adhesive or flanged joints.

G. Condensate piping below grade, [NPS 2 (DN 50)] <Insert pipe size range> and smaller, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

2. RTRP and RTRF with adhesive or flanged joints.

Retain "either of" option in paragraph below to allow Contractor to select piping materials from those retained.

H. Condensate piping below grade, [NPS 2-1/2 (DN 65)] <Insert pipe size range> and larger, shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both, and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Schedule 80, Type E, Grade B, steel pipe; Class 150 wrought-steel fittings, flanges, and flange fittings; and welded and flanged joints.

2. RTRP and RTRF with adhesive or flanged joints.

3.3 ANCILLARY PIPING APPLICATIONS

Retain "either of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Makeup-water piping installed above grade shall be[ either of] the following:

Retain one or both subparagraphs below.  If retaining both and it is not the intent to give the Contractor the option to select materials, delete the "either of" option in paragraph above and identify each material on Drawings.  Show points of transition from one material to another.

1. Drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] joints.

2. Schedule [40] [80] CPVC plastic pipe and fittings, and solvent welded joints.

B. Makeup-Water Piping Installed below Grade and within Slabs:  Annealed-temper copper tubing, wrought-copper fittings, and soldered joints.  Use the fewest possible joints.

C. Blowdown-Drain Piping:  Same materials and joining methods as for piping specified for the service in which blowdown drain is installed.

D. Air-Vent Piping:

1. Inlet:  Same as service where installed.

2. Outlet:  Type K (A) annealed-temper copper tubing with soldered or flared joints.

E. Vacuum-Breaker Piping:  Outlet, same as service where installed.

F. Safety-Valve-Inlet and -Outlet Piping:  Same materials and joining methods as for piping specified for the service in which safety valve is installed.

3.4 VALVE APPLICATIONS

A. Install shutoff duty valves at branch connections to steam supply mains, at steam supply connections to equipment, and at the outlet of steam traps.

B. Install safety valves on pressure-reducing stations and elsewhere as required by ASME Boiler and Pressure Vessel Code.  Install safety-valve discharge piping, without valves, to nearest floor drain or as indicated on Drawings.  Comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1, for installation requirements.

3.5 PIPING INSTALLATION

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Use indicated piping locations and arrangements if such were used to size pipe and calculate friction loss, expansion, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

B. Install piping in concealed locations, unless otherwise indicated and except in equipment rooms and service areas.

C. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

D. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

E. Install piping to permit valve servicing.

F. Install piping free of sags and bends.

G. Install fittings for changes in direction and branch connections.

H. Install piping to allow application of insulation.

I. Select system components with pressure rating equal to or greater than system operating pressure.

J. Install groups of pipes parallel to each other, spaced to permit applying insulation and servicing of valves.

K. Install drains, consisting of a tee fitting, NPS 3/4 (DN 20) full port-ball valve, and short NPS 3/4 (DN 20) threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.

L. Install steam supply piping at a minimum uniform grade of 0.2 percent downward in direction of steam flow.

M. Install condensate return piping at a minimum uniform grade of 0.4 percent downward in direction of condensate flow.

N. Reduce pipe sizes using eccentric reducer fitting installed with level side down.

O. Install branch connections to mains using[ mechanically formed] tee fittings in main pipe, with the branch connected to top of main pipe.

P. Install valves according to Division 23 Section "General-Duty Valves for HVAC Piping."

Q. Install unions in piping, NPS 2 (DN 50) and smaller, adjacent to valves, at final connections of equipment, and elsewhere as indicated.

R. Install flanges in piping, NPS 2-1/2 (DN 65) and larger, at final connections of equipment and elsewhere as indicated.

S. Install strainers on supply side of control valves, pressure-reducing valves, traps, and elsewhere as indicated.  Install NPS 3/4 (DN 20) nipple and full port ball valve in blowdown connection of strainers NPS 2 (DN 50) and larger.  Match size of strainer blowoff connection for strainers smaller than NPS 2 (DN 50).

T. Install expansion loops, expansion joints, anchors, and pipe alignment guides as specified in Division 23 Section "Expansion Fittings and Loops for HVAC Piping."

U. Identify piping as specified in Division 23 Section "Identification for HVAC Piping and Equipment."

V. Install drip legs at low points and natural drainage points such as ends of mains, bottoms of risers, and ahead of pressure regulators, and control valves.

1. On straight runs with no natural drainage points, install drip legs at intervals not exceeding [300 feet (90 m)] <Insert distance>.

2. Size drip legs same size as main.  In steam mains NPS 6 (DN 150) and larger, drip leg size can be reduced, but to no less than NPS 4 (DN 100).

Retain paragraph and subparagraphs below if flash tanks are required.

W. Flash Tank:

1. Pitch condensate piping down toward flash tank.

2. If more than one condensate pipe discharges into flash tank, install a check valve in each line.

3. Install thermostatic air vent at tank top.

4. Install safety valve at tank top.

5. Install full-port ball valve, and swing check valve on condensate outlet.

6. Install inverted bucket or float and thermostatic trap at low-pressure condensate outlet, sized for three times the calculated heat load.

Retain subparagraph below if flash tanks are required to recover low-pressure steam.

7. Install pressure gage on low-pressure steam outlet according to Division 23 Section "Meters and Gages for HVAC Piping."

3.6 STEAM-TRAP INSTALLATION

A. Install steam traps in accessible locations as close as possible to connected equipment.

B. Install full-port ball valve, strainer, and union upstream from trap; install union, check valve, and full-port ball valve downstream from trap unless otherwise indicated.

3.7 PRESSURE-REDUCING VALVE INSTALLATION

Consult manufacturers for proper installation of piping to and from pressure-reducing valves.

A. Install pressure-reducing valves in accessible location for maintenance and inspection.

B. Install bypass piping around pressure-reducing valves, with globe valve equal in size to area of pressure-reducing valve seat ring, unless otherwise indicated.

C. Install gate valves on both sides of pressure-reducing valves.

D. Install unions or flanges on both sides of pressure-reducing valves having threaded- or flanged-end connections respectively.

E. Install pressure gages on low-pressure side of pressure-reducing valves after the bypass connection according to Division 23 Section "Meters and Gages for HVAC Piping."

F. Install strainers upstream for pressure-reducing valve.

G. Install safety valve downstream from pressure-reducing valve station.

3.8 STEAM OR CONDENSATE METER INSTALLATION

A. Install meters with lengths of straight pipe upstream and downstream according to steam meter manufacturer's instructions.

B. Provide data acquisition wiring.  Refer to Division 23 Section "Instrumentation and Control for HVAC."

3.9 SAFETY VALVE INSTALLATION

Retain first option in first paragraph below for HP systems; retain second option for LP systems; retain third option for combination HP and LP systems.

A. Install safety valves according to [ASME B31.1, "Power Piping." ] [ASME B31.9, "Building Services Piping." ] [ASME B31.1, "Power Piping" and ASME B31.9, "Building Services Piping." ]

B. Pipe safety-valve discharge without valves to atmosphere outside the building.

C. Install drip-pan elbow fitting adjacent to safety valve and pipe drain connection to nearest floor drain.

D. Install exhaust head with drain to waste, on vents equal to or larger than NPS 2-1/2 (DN 65).

3.10 HANGERS AND SUPPORTS

Piping support must account for expansion and contraction, vibration, dead load of piping and its contents, and seismic-bracing requirements.

A. Install hangers and supports according to Division 23 Section "Hangers and Supports for HVAC Piping and Equipment."  Comply with requirements below for maximum spacing.

Retain first paragraph below for projects in areas that require seismic restraints.

B. Seismic restraints are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal piping less than 20 feet (6 m) long.

2. Adjustable roller hangers and spring hangers for individual horizontal piping 20 feet (6 m) or longer.

3. Pipe Roller:  MSS SP-58, Type 44 for multiple horizontal piping 20 feet (6 m) or longer, supported on a trapeze.

4. Spring hangers to support vertical runs.

Verify actual supported loads for hanger sizes and spacing.  Consult structural engineer.  Spacing and sizes in first two paragraphs and associated subparagraphs below are from the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment."

D. Install hangers with the following maximum spacing and minimum rod sizes:

1. NPS 3/4 (DN 20):  Maximum span, 9 feet (2.7 m); minimum rod size, 1/4 inch (6.4 mm).

2. NPS 1 (DN 25):  Maximum span, 9 feet (2.7 m); minimum rod size, 1/4 inch (6.4 mm).

3. NPS 1-1/2 (DN 40):  Maximum span, 12 feet (3.7 m); minimum rod size, 3/8 inch (10 mm).

4. NPS 2 (DN 50):  Maximum span, 13 feet (4 m); minimum rod size, 3/8 inch (10 mm).

5. NPS 2-1/2 (DN 65):  Maximum span, 14 feet (4.3 m); minimum rod size, 3/8 inch (10 mm).

6. NPS 3 (DN 80):  Maximum span, 15 feet (4.6 m); minimum rod size, 3/8 inch (10 mm).

7. NPS 4 (DN 100):  Maximum span, 17 feet (5.2 m); minimum rod size, 1/2 inch (13 mm).

8. NPS 6 (DN 150):  Maximum span, 21 feet (6.4 m); minimum rod size, 1/2 inch (13 mm).

9. NPS 8 (DN 200):  Maximum span, 24 feet (7.3 m); minimum rod size, 5/8 inch (16 mm).

10. NPS 10 (DN 250):  Maximum span, 26 feet (8 m); minimum rod size, 3/4 inch (19 mm).

11. NPS 12 (DN 300):  Maximum span, 30 feet (9.1 m); minimum rod size, 7/8 inch (22 mm).

12. NPS 14 (DN 350):  Maximum span, 32 feet (9.8 m); minimum rod size, 1 inch (25 mm).

13. NPS 16 (DN 400):  Maximum span, 35 feet (10.7 m); minimum rod size, 1 inch (25 mm).

14. NPS 18 (DN 450):  Maximum span, 37 feet (11.3 m); minimum rod size, 1-1/4 inches (32 mm).

15. NPS 20 (DN 500):  Maximum span, 39 feet (11.9 m); minimum rod size, 1-1/4 inches (32 mm).

E. Install hangers for drawn-temper copper piping with the following maximum spacing and minimum rod sizes:

1. NPS 1/2 (DN 15):  Maximum span, 4 feet (1.2 m); minimum rod size, 1/4 inch (6.4 mm).

2. NPS 3/4 (DN 20):  Maximum span, 5 feet (1.5 m); minimum rod size, 1/4 inch (6.4 mm).

3. NPS 1 (DN 25):  Maximum span, 6 feet (1.8 m); minimum rod size, 1/4 inch (6.4 mm).

4. NPS 1-1/2 (DN 40):  Maximum span, 8 feet (2.4 m); minimum rod size, 3/8 inch (10 mm).

5. NPS 2 (DN 50):  Maximum span, 8 feet (2.4 m); minimum rod size, 3/8 inch (10 mm).

6. NPS 2-1/2 (DN 65):  Maximum span, 9 feet (2.7 m); minimum rod size, 3/8 inch (10 mm).

7. NPS 3 (DN 80):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (10 mm).

F. Support vertical runs at roof, at each floor, and at 10-foot (3-m) intervals between floors.

Retain paragraph below for fiberglass piping.

G. Fiberglass Piping Hanger Spacing:  Space hangers according to pipe manufacturer's written instructions for service conditions.  Avoid point loading.  Space and install hangers with the fewest practical rigid anchor points.

3.11 PIPE JOINT CONSTRUCTION

A. Join pipe and fittings according to the following requirements and Division 23 Sections specifying piping systems.

B. Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

C. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

D. Soldered Joints:  Apply ASTM B 813, water-flushable flux, unless otherwise indicated, to tube ends.  Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B 32.

E. Brazed Joints:  Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" chapter, using copper-phosphorus brazing filler metal complying with AWS A5.8.

F. Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

G. Welded Joints:  Construct joints according to AWS D10.12 (AWS D10.12M), using qualified processes and welding operators according to Part 1 "Quality Assurance" Article.

H. Flanged Joints:  Select appropriate gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.  Use suitable lubricants on bolt threads.

Retain paragraph below for fiberglass pipe assembly.

I. Fiberglass Bonded Joints:  Prepare pipe ends and fittings, apply adhesive, and join according to pipe manufacturer's written instructions.

3.12 TERMINAL EQUIPMENT CONNECTIONS

A. Size for supply and return piping connections shall be the same as or larger than equipment connections.

Specify access doors and panels for walls and ceilings in Division 08 Section "Access Doors and Frames."  Show locations of access doors and panels on Drawings, and coordinate with architectural reflected ceiling and wall elevation drawings.

B. Install traps and control valves in accessible locations close to connected equipment.

C. Install bypass piping with globe valve around control valve.  If parallel control valves are installed, only one bypass is required.

D. Install vacuum breakers downstream from control valve, close to coil inlet connection.

E. Install a drip leg at coil outlet.

3.13 FIELD QUALITY CONTROL

A. Prepare steam and condensate piping according to [ASME B31.1, "Power Piping" ] [and] [ASME B31.9, "Building Services Piping," ] and as follows:

1. Leave joints, including welds, uninsulated and exposed for examination during test.

2. Provide temporary restraints for expansion joints that cannot sustain reactions due to test pressure.  If temporary restraints are impractical, isolate expansion joints from testing.

3. Flush system with clean water.  Clean strainers.

4. Isolate equipment from piping.  If a valve is used to isolate equipment, its closure shall be capable of sealing against test pressure without damage to valve.  Install blinds in flanged joints to isolate equipment.

B. Perform the following tests on steam and condensate piping:

Procedures in subparagraphs below are paraphrased from ASME B31.9.

1. Use ambient temperature water as a testing medium unless there is risk of damage due to freezing.  Another liquid that is safe for workers and compatible with piping may be used.

2. Subject piping system to hydrostatic test pressure that is not less than 1.5 times the working pressure.  Test pressure shall not exceed maximum pressure for any vessel, pump, valve, or other component in system under test.  Verify that stress due to pressure at bottom of vertical runs does not exceed 90 percent of specified minimum yield strength.

3. After hydrostatic test pressure has been applied for at least 10 minutes, examine piping, joints, and connections for leakage.  Eliminate leaks by tightening, repairing, or replacing components, and repeat hydrostatic test until there are no leaks.

C. Prepare written report of testing.

END OF SECTION 23 2213

	STEAM AND CONDENSATE HEATING PIPING
	232213 - 1



