Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236413.16 - INDIRECT-FIRED ABSORPTION WATER CHILLERS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Packaged, water-cooled, [single-] [and] [double-]effect absorption chillers.

2. Heat-exchanger, brush-cleaning system.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. BAS:  Building automation system.

B. COP:  Coefficient of performance.  The ratio of the rate of heat removal to the rate of energy input using consistent units for any given set of rating conditions.

C. IPLV:  Integrated part-load value.  A single-number part-load efficiency figure of merit calculated per the method defined by ARI 560 and referenced to ARI standard rating conditions.

D. NPLV:  Nonstandard part-load value.  A single-number part-load efficiency figure of merit calculated per the method defined by ARI 560 and intended for operating conditions other than the ARI standard rating conditions.

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph below with "Seismic Qualifications Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

A. Seismic Performance:  Indirect-fired absorption chillers shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

B. Condenser-Fluid Temperature Performance:

1. Startup Condenser-Fluid Temperature:  Chiller shall be capable of starting with an entering condenser-fluid temperature of [60 deg F (16 deg C)] [55 deg F (13 deg C)] [40 deg F (4.4 deg C)] <Insert temperature> and providing stable operation until the system temperature is elevated to the minimum operating entering condenser-fluid temperature.

2. Minimum Operating Condenser-Fluid Temperature:  Chiller shall be capable of continuous operation over the entire capacity range indicated with an entering condenser-fluid temperature of [65 deg F (18 deg C)] [60 deg F (16 deg C)] [55 deg F (13 deg C)].

3. Make factory modifications to standard chiller design if necessary to comply with performance indicated.

C. Site Altitude:  Chiller shall be suitable for altitude at which installed without affecting performance indicated.  Make adjustments to affected chiller components to account for site altitude.

Retain paragraph below if Project requires more stringent tolerances than allowed by ARI 560.

D. Performance Tolerance:  Comply with the following in lieu of ARI 560:

1. Allowable Capacity Tolerance:  [Zero] <Insert number> percent.

2. Allowable IPLV/NPLV Performance Tolerance:  [Zero] <Insert number> percent.

1.5 SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, furnished specialties and accessories.

1. Performance at ARI standard conditions and at conditions indicated.

2. Performance at ARI standard unloading conditions.

3. Minimum evaporator flow rate.

4. Absorbent capacity of chiller.

5. Refrigerant capacity of chiller.

6. Fluid capacity of evaporator and condenser.

7. Fluid capacity of generator.

8. Characteristics of safety relief devices.

9. Minimum entering condenser-fluid temperature.

10. Performance at varying capacities with constant design condenser-fluid temperature.  Repeat performance at varying capacities for different condenser-fluid temperatures from design to minimum in [5 deg F (3 deg C)] <Insert temperature> increments.

Retain first paragraph below if applying for LEED certification.

B. LEED Submittals:

1. Product Data for LEED-NC Prerequisite EA 2:  Documentation indicating that units comply with ASHRAE 90.1-2004.

2. Product Data for LEED-NC Prerequisite EA 3:  Documentation indicating that refrigerants comply.

3. Product Data for LEED-NC Credit EA 4:  Documentation indicating that equipment and refrigerants comply.

C. Shop Drawings:  Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, load distribution, required clearances, method of field assembly, components, and location and size of each field connection.

2. Wiring Diagrams:  For power, signal, and control wiring.

3. Insulated Surface Diagrams:  Indicating cold and hot surfaces requiring insulation with area tabulated for each.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Floor plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Structural supports.

2. Piping roughing-in requirements.

3. Wiring roughing-in requirements, including spaces reserved for electrical equipment.

4. Access requirements, including working clearances for mechanical controls and electrical equipment, and tube pull and service clearances.

Retain first paragraph below if retaining certification in "Quality Assurance" Article.

E. Certificates:  For certification required in "Quality Assurance" Article.

Some manufacturers will not provide certification specified in first paragraph below.  Verify availability with manufacturers and retain below if required by seismic criteria applicable to Project.  See the "Seismic Considerations" Article in the Evaluations.  Coordinate below with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." See ASCE/SEI 7 for certification requirements for equipment and components.

F. Seismic Qualification Certificates:  For chillers, accessories, and components, from manufacturer.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

G. Source quality-control reports.

H. Startup service reports.

I. Operation and Maintenance Data:  For each chiller to include in emergency, operation, and maintenance manuals.

J. Warranty:  Sample of special warranty.

1.6 QUALITY ASSURANCE

A. ARI Rating:  Rate chiller performance according to requirements in ARI 560.

B. ASHRAE Compliance:

1. ASHRAE 15 for safety code for mechanical refrigeration.

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

2. ASHRAE/IESNA 90.1-2004.

C. ASME Compliance:  Fabricate and label chiller pressure vessels to comply with applicable portions of ASME Boiler and Pressure Vessel Code.

D. Comply with NFPA 70.

E. Comply with requirements of UL and UL Canada, and include label by a qualified testing agency showing compliance.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Ship chillers factory charged with nitrogen.

Retain one of first two paragraphs below.  First paragraph is least restrictive; second paragraph is limiting.  Carrier ships single-piece chillers charged with absorbent and ships two-piece chillers with absorbent shipped separately.  Trane ships absorbent separate from chillers.  YORK ships single-effect absorption chillers without absorbent; absorbent is shipped separately.  YORK ships double-effect chillers as a one-piece assembly with both absorbent and refrigerant installed.

B. Ship absorbent and refrigerant in chillers or in containers separate from chillers.

C. Ship [absorbent] [and] [refrigerant] in containers separate from chillers.

Retain paragraph below only for projects with special shipping requirements.  Export shipping adds cost.

D. Package chiller for export shipping in totally enclosed [bagging] [crate] [crate with bagging].

1.8 COORDINATION

Retain first paragraph below for mounting chillers on concrete bases.

A. Coordinate sizes and locations of concrete bases with actual equipment provided.  Cast anchor-bolt inserts into bases.

Retain paragraph below for mounting chillers on a structural-steel support structure.

B. Coordinate sizes, locations, and anchoring attachments of structural-steel support structures.

1.9 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of chillers that fail in materials or workmanship within specified warranty period.

Consult Owner about need for extended warranties.

1. Extended warranties include, but are not limited to, the following:

Retain one of first three subparagraphs below.

a. Complete chiller.

b. [Pumps and motors] [Purge unit] <Insert components>.

c. [Absorbent] [Absorbent and refrigerant] only.

d. Parts [only] [and labor].

e. Loss of absorbent and refrigerant for any reason.

Verify available warranties and warranty periods with manufacturers listed in Part 2.

B. Warranty Period:  [Two] [Three] [Four] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two paragraphs and list of manufacturers in this article.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Manufacturers listed in subparagraphs below offer single-effect models for use with hot water and steam.  YORK offers a double-effect model for use only with steam.  Trane offers a double-effect model for use with hot water and steam.  See Evaluations.

1. Carrier Corporation; a United Technologies company.

2. Trane; a division of American Standard.

3. YORK; a Johnson Controls company.

4. <Insert manufacturer's name>.

2.2 MANUFACTURED UNIT

A. Description:  Factory-assembled and -tested, hermetic-design chiller complete with absorber, evaporator, condenser, generator, solution heat exchanger, controls, absorbent solution pump with motor, refrigerant pump with motor, purge unit with motor, motor controllers, rupture disk, interconnecting unit piping and wiring, indicated accessories, and mounting frame.

Retain subparagraph below if limited space is available for installation.

1. Disassemble chiller into major assemblies as required by the installation after factory testing and before packaging for shipment.

B. Absorbent and Refrigerant:

1. Absorbent:  Lithium bromide solution with corrosion inhibitor.

2. Refrigerant:  Deionized [or distilled ]water.

3. Performance Enhancer:  Heat and mass transfer enhancer to improve performance.

Retain paragraph below for projects in seismic areas.  If retaining, also retain "Seismic Performance" Paragraph in "Performance Requirements" Article and "Seismic Qualification Certificates" Paragraph in "Submittals" Article.

C. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to chiller, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

2.3 PUMPS

A. Hermetically sealed, self-lubricating, and fitted with self-adjusting, spring-loaded, wear-compensating tapered carbon bearings.

Equipment from listed manufacturers complies with first option in first paragraph below.  Standard equipment from YORK and Trane complies with second option.

B. Pump motor assembly shall be designed to operate for not less than [25,000] [50,000] hours between inspections.

C. Pump motors cooled, and bearings lubricated, either by fluid being pumped or by a filtered supply of liquid refrigerant.

D. Pump suction and discharge equipped with isolation valves.

E. Separate and dedicated pumps for absorbent solution and refrigerant.

1. Absorbent solution and refrigerant flow-control method shall be manufacturer's choice to comply with operating requirements indicated.

F. Purge System:  Unit mounted and factory wired, equipped with controls and a pump to automatically remove noncondensable vapors.

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. Purge Pump Motor:  Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Retain first or second option in subparagraph below to restrict enclosure type; retain third option to allow Contractor the choice.  If retaining first or second option, verify enclosure types available from manufacturer.

a. Enclosure:  [Open dripproof] [Totally enclosed] [Open dripproof or totally enclosed].

2.4 HEAT-EXCHANGER SHELLS

Retain one of first two paragraphs below.

A. Configuration for Single-Effect Chillers:  Two shells; one shell consists of the absorber/evaporator and the other shell consists of the condenser/generator.

B. Configuration for Double-Effect Chillers:  Two shells; one shell consists of the absorber/evaporator, low-stage generator/condenser and the other shell consists of the high-stage generator.

C. Construction:  Fabricated from continuously welded carbon-steel sheet or plate, or from seamless pipe.

D. Design Pressure and Temperature Rating:  Comply with applicable requirements in ASME Boiler and Pressure Vessel Code.

E. End Tube Sheets:  Carbon-steel plates continuously welded to each end of shell; drilled and reamed to accommodate tubes with positive seal between fluid in tubes and refrigerant in shell.

F. Intermediate Tube Sheets:  Carbon-steel plates installed in shell and spaced along length of tube at intervals required to eliminate vibration and to avoid contact of tubes resulting in abrasion and wear.

G. Generator/Condenser Shell Pressure Relief Device:  Manufacturers standard rupture disk complying with requirements in ASHRAE 15 and in applicable portions of ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

2.5 ABSORBER

A. Nozzle or Dispersion Trays:  Designed to evenly distribute absorbent solution over tubes.  Constructed of brass, stainless steel, or another material that will not corrode.

B. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets.  Replaceable from either end and without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger.  Tube materials vary among manufacturers and chiller models; verify availability with manufacturer.  First option in first subparagraph below is current standard of listed manufacturers.

Copper-nickel alloys available include 95/5 and 90/10.  The higher nickel content in 90/10 provides better resistance to corrosion.  If required by Project, insert specific alloy.

Stainless-steel types available include Types 304L and 316L.  The higher nickel content in Type 316L provides better resistance to corrosion.  If required by Project, insert specific type.

2. Material:  [Copper] [Copper-nickel alloy] [Stainless steel] [Titanium] [Copper, copper-nickel alloy, stainless steel, or titanium] <Insert material>.

Retain one of four options in first subparagraph below.  First option gives manufacturer the choice; second, third, and fourth options limit thickness.  Second option is current standard of listed manufacturers but is subject to change.  Third and fourth options are upgrades.  If using materials other than copper, wall thickness may vary.  See Evaluations.

3. Minimum Wall Thickness:  [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish:  Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers.  Second option is for applications with dirty fluids that require frequent tube cleaning.  Third option gives manufacturer the choice.

5. Internal Finish:  [Enhanced] [Smooth] [Enhanced or smooth].

C. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

Retain one of first two subparagraphs below.  If retaining first subparagraph, confirm availability of second option with manufacturers.  Not all manufacturers offer second option with pressure rating greater than 150 psig (1035 kPa).

2. [Standard] [Marine] type for water box with piping connections.

a. Water boxes [and marine water-box covers ]shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine water-box covers.

3. Standard type for water box without piping connections.

a. Water boxes shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine water-box covers.

4. Nozzle Pipe Connections:  [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [1-inch (25-mm)] [3/4- or 1-inch (19- or 25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain first paragraph below for special applications.  Verify availability with manufacturers.

D. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid.  Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

Retain paragraph below for factory involvement with crossover pipe between absorber and condenser.  First option is YORK's standard offering on double-effect chillers and Carrier's standard offering on single-effect chillers.  Second option is Trane's standard offering on double-effect chillers and a standard factory option on single-effect chillers.

E. Absorber/Condenser Crossover Piping:  Factory [furnished] [installed] piping connecting fluid connection of absorber discharge to condenser inlet.

2.6 EVAPORATOR

A. Nozzle or Dispersion Trays:  Designed to evenly distribute refrigerant over tubes.  Constructed of brass, stainless steel, or another material that will not corrode.

First option in first paragraph below is Trane's standard offering.  Second option is YORK's standard offering and Trane's factory option.

B. Refrigerant Holding Pan:  [Steel] [Stainless steel] [Steel or stainless steel].

C. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets.  Replaceable from either end and without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger.  Tube materials vary among manufacturers and chiller models; verify availability with manufacturer.  First option in first subparagraph below is current standard of listed manufacturers.

Copper-nickel alloys available include 95/5 and 90/10.  The higher nickel content in 90/10 provides better resistance to corrosion.  If required by Project, insert specific alloy.

Stainless-steel types available include Types 304L and 316L.  The higher nickel content in Type 316L provides better resistance to corrosion.  If required by Project, insert specific type.

2. Material:  [Copper] [Copper-nickel alloy] [Stainless steel] [Titanium] [Copper, copper-nickel alloy, stainless steel, or titanium] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; second, third, and fourth options limit thickness.  Second option is current standard of listed manufacturers but is subject to change.  Third and fourth options are upgrades.  If using materials other than copper, wall thickness may vary.  See Evaluations.

3. Minimum Wall Thickness:  [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish:  Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers.  Second option is for applications with dirty fluids that require frequent tube cleaning.  Third option gives manufacturer the choice.

5. Internal Finish:  [Enhanced] [Smooth] [Enhanced or smooth].

D. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

Retain one of first two subparagraphs below.  If retaining first subparagraph, confirm availability of second option with manufacturers.  Not all manufacturers offer second option for the evaporator and some manufacturers do not offer second option with pressure rating greater than 150 psig (1035 kPa).

2. [Standard] [Marine] type for water box with piping connections.

a. Water boxes [and marine water-box covers ]shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine water-box covers.

3. Standard type for water box without piping connections.

a. Water boxes shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine water-box covers.

4. Nozzle Pipe Connections:  [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [1-inch (25-mm)] [3/4- or 1-inch (19- or 25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

2.7 CONDENSER

First option in first paragraph below is Trane's standard offering.  Second option is YORK's standard offering and Trane's factory option.

A. Refrigerant Holding Pan:  [Steel] [Stainless steel] [Steel or stainless steel].

B. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets.  Replaceable from either end and without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger.  Tube materials vary among manufacturers and chiller models; verify availability with manufacturer.  First option in first subparagraph below is current standard of listed manufacturers.

Copper-nickel alloys available include 95/5 and 90/10.  The higher nickel content in 90/10 provides better resistance to corrosion.  If required by Project, insert specific alloy.

Stainless-steel types available include Types 304L and 316L.  The higher nickel content in Type 316L provides better resistance to corrosion.  If required by Project, insert specific type.

2. Material:  [Copper] [Copper-nickel alloy] [Stainless steel] [Titanium] [Copper, copper-nickel alloy, stainless steel, or titanium] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; second, third, and fourth options limit thickness.  Second option is current standard of listed manufacturers but is subject to change.  Third and fourth options are upgrades.  If using materials other than copper, wall thickness may vary.  See Evaluations.

3. Minimum Wall Thickness:  [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish:  Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers.  Second option is for applications with dirty fluids that require frequent tube cleaning.  Third option gives manufacturer the choice.

5. Internal Finish:  [Enhanced] [Smooth] [Enhanced or smooth].

C. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

Retain one of first two subparagraphs below.  If retaining first subparagraph, confirm availability of second option with manufacturers.  Not all manufacturers offer second option with pressure rating greater than 150 psig (1035 kPa).

2. [Standard] [Marine] type for water box with piping connections.

a. Water boxes [and marine water-box covers ]shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine water-box covers.

3. Standard type for water box without piping connections.

a. Water boxes shall have lifting lugs or eyebolts.

Retain one of first two subparagraphs below for special applications.

b. [Hinged] [or] [davited] water boxes.

c. [Hinged] [or] [davited] marine water-box covers.

4. Nozzle Pipe Connections:  [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [1-inch (25-mm)] [3/4- or 1-inch (19- or 25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain paragraph below for special applications.

D. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid.  Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

2.8 GENERATOR FOR SINGLE-EFFECT CHILLERS

A. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets.  Replaceable from either end and without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger.  Tube materials vary among manufacturers and chiller models; verify availability with manufacturer.  First option in first subparagraph below is current standard of listed manufacturers.

Stainless-steel types available include Types 316L and 409.  The higher nickel content in Type 316L provides better resistance to corrosion.  If required by Project, insert specific type of stainless steel.

2. Material:  [90/10 copper-nickel alloy] [Stainless steel] [Titanium] [90/10 copper-nickel alloy, stainless steel, or titanium] <Insert material>.

Retain one of two options in first subparagraph below.  First option gives manufacturer the choice; second option limits thickness.  Second option is current standard of listed manufacturers but is subject to change.  If using materials other than 90/10 copper-nickel alloy, wall thickness may vary.  See Evaluations.

3. Minimum Wall Thickness:  [Manufacturer's choice] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish:  Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers.  Second option gives manufacturer the choice.

5. Internal Finish:  [Smooth] [Enhanced or smooth].

B. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

2. Standard type water box.

3. Water boxes shall have lifting lugs or eyebolts.

4. Nozzle Pipe Connections:  [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [1-inch (25-mm)] [3/4- or 1-inch (19- or 25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain paragraph below for special applications.  Verify availability with manufacturers.

C. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid.  Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

2.9 FIRST-STAGE GENERATOR FOR DOUBLE-EFFECT CHILLERS

A. Tubes:

1. Replaceable, straight, or U tubes expanded into tube sheets.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger.  First option in first subparagraph below gives manufacturer the choice; other options limit material choice.  Tube materials vary among manufacturers and chiller models; verify availability with manufacturer.  Second option in first subparagraph below is YORK's standard offering and third option is Trane's standard offering.  Fourth option is an upgrade.

2. Material:  [Manufacturer's standard] [70/30 copper-nickel alloy] [Type 409 stainless steel] [Titanium] [70/30 copper-nickel alloy, Type 409 stainless steel] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness.  Second option is Trane's standard offering with stainless-steel tubes.  Third option is YORK's standard offering with copper-nickel-alloy tubes.

3. Minimum Wall Thickness:  [Manufacturer's choice] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish:  Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers.  Second option gives manufacturer the choice.

5. Internal Finish:  [Smooth] [Enhanced or smooth].

B. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

2. Standard type water box.

3. Water boxes shall have lifting lugs or eyebolts.

4. Nozzle Pipe Connections:  [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [1-inch (25-mm)] [3/4- or 1-inch (19- or 25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain paragraph below for special applications.  Verify availability with manufacturers.

C. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid.  Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

2.10 SECOND-STAGE GENERATOR FOR DOUBLE-EFFECT CHILLERS

A. Tubes:

1. Individually replaceable, straight tubes expanded into tube sheets.  Replaceable from either end and without damage to tube sheets and other tubes.

Tube materials for all heat exchangers can be independently selected; the choice can be different for each heat exchanger.  Tube materials vary among manufacturers and chiller models; verify availability with manufacturer.  First option in first subparagraph below is YORK's standard offering; second option is Trane's standard offering.

2. Material:  [Copper] [Copper-nickel alloy] [Copper or copper-nickel alloy] [Stainless steel] [Titanium] <Insert material>.

First option in first subparagraph below gives manufacturer the choice; other options limit thickness.  Second option is YORK's standard offering and third option is Trane's standard offering.

3. Minimum Wall Thickness:  [Manufacturer's choice] [0.025 inch (0.6 mm)] [0.028 inch (0.7 mm)] [0.035 inch (0.9 mm)] <Insert dimension>.

4. External Finish:  Manufacturer's standard.

First option in subparagraph below is standard of most manufacturers.  Second option gives manufacturer the choice.

5. Internal Finish:  [Smooth] [Enhanced or smooth].

B. Water Boxes:

1. Carbon-steel construction; arranged to provide visual inspection and cleaning of tubes from either end without disturbing refrigerant in shell.

2. Standard type water box.

3. Water boxes shall have lifting lugs or eyebolts.

4. Nozzle Pipe Connections:  [Welded, ASME B16.5, flat-face flange] [Welded, ASME B16.5, raised-face flange] [Grooved for mechanical-joint coupling] [Grooved with mechanical-joint coupling and flange adapter].

5. Thermistor or RTD temperature sensor factory installed in each nozzle.

6. Fit each water box with [3/4-inch (19-mm)] [1-inch (25-mm)] [3/4- or 1-inch (19- or 25-mm)] <Insert dimension> drain connection at low point and vent connection at high point, each with threaded plug.

Retain paragraph below for special applications.  Verify availability with manufacturers.

C. Additional Corrosion Protection:

1. Electrolytic corrosion-inhibitor anode.

Retain one of two subparagraphs below.

2. Coat wetted surfaces with a corrosion-resistant finish.

3. Using same material as tubes, clad surfaces of end tube sheets in contact with fluid.  Coat other wetted surfaces, including water boxes, with a corrosion-resistant finish.

2.11 SOLUTION HEAT EXCHANGER

A. Description:  Shell-and-tube or brazed-plate heat exchanger; integral part of chiller to increase cycle efficiency by preheating the weak solution on its way to the generator while precooling the strong solution returning from the generator.

2.12 STEAM CONDENSATE DRAIN COOLER

Retain this article for factory-installed drain cooler on double-effect chillers fed with steam.  YORK's double-effect chiller equipped with drain cooler is standard.  Consult other manufacturers for availability.

A. Description:  Shell-and-tube heat exchanger constructed of carbon-steel shell and copper-nickel-alloy or stainless-steel tubes.

2.13 FACTORY-APPLIED INSULATION

Factory-applied insulation on cold surfaces is an optional feature offered by YORK on its single-effect absorption chiller models and by Trane on all its models.  YORK does not offer factory-applied insulation on its double-effect absorption chiller model.  Carrier does not offer factory-applied insulation on its absorption chiller models.

A. Factory-Applied Insulation on Cold Surfaces:

1. Closed-cell, flexible elastomeric thermal insulation complying with ASTM C 534, Type I for tube and Type II for sheet materials.

Second option in first subparagraph below may not be available from some manufacturers as a standard factory option.  Consult manufacturers.

a. Thickness:  [3/4 inch (19 mm)] [1-1/2 inches (38 mm)] <Insert dimension>.

2. Adhesive:  As recommended by insulation manufacturer.

3. Factory apply insulation over all cold surfaces of chiller capable of forming condensation.  Components shall include, but not be limited to, evaporator shell and end tube sheets; evaporator water boxes including nozzles; refrigerant pump; cold surfaces of motor; and cold piping.

a. Apply adhesive to 100 percent of insulation contact surface.

b. Before insulating steel surfaces, prepare surfaces for paint, and prime and paint as indicated for other painted components.  Do not insulate unpainted steel surfaces.

c. Seal seams and joints to provide a vapor barrier.

d. After adhesive has fully cured, paint exposed surfaces of insulation to match other painted parts.

Trane offers an option for factory-applied insulation on hot surfaces of its double-effect absorption chiller model, but not its single-effect absorption chiller models.  Carrier and YORK do not offer an option for factory-applied insulation on hot surfaces of their absorption chillers.

B. Factory-Applied Insulation on Hot Surfaces:

1. Mineral-fiber board, pipe or tank insulation complying with one of following:

a. ASTM C 547, Type I or Type II, Grade A.

b. ASTM C 612, Type IB.

c. ASTM C 1393, Type II or Type IIIA, Category 2.

Consult manufacturer for available thicknesses.

d. Thickness:  [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert dimension>.

2. Adhesive:  As recommended by insulation manufacturer.

3. Factory apply materials over all hot surfaces to provide smooth, straight, and even surfaces; free of voids.

a. Apply adhesive to insulation contact surface as recommended by insulation manufacturer.

b. Install insulation anchor pins and washers if required by insulation manufacturer to secure insulation to surfaces to be insulated.

c. Completely encapsulate insulation with metal jacket, leaving no exposed insulation.  Provide removable jacket on components requiring access for service and inspection.

d. Paint exposed surfaces of metal jacket to match other painted parts unless jacket material is aluminum or stainless steel.

2.14 ELECTRICAL

A. Factory installed and wired, and functionally tested at factory before shipment.

Retain first paragraph below for single-point, field-power connection.  Requirement is limited to chillers equipped with factory-mounted motor controllers.

B. Single-point, field-power connection to [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].  Minimum withstand rating shall be as required by electrical power distribution system, but not less than [42,000] [65,000] <Insert value> A.

1. Branch power circuit to each motor, dedicated electrical load, and controls[ with disconnect switch or circuit breaker].

If retaining option in subparagraph above, retain first two subparagraphs below.

a. NEMA KS 1, heavy-duty, fusible switch with rejection-type fuse clips rated for fuses.  Select and size fuses to provide Type 2 protection according to IEC 60947-4-1.

b. NEMA AB 1, motor-circuit protector (circuit breaker) with field-adjustable, short-circuit-trip set point.

2. NEMA ICS 2, Class A, full-voltage, nonreversing motor controller, hand-off-auto switch, and overcurrent protection for each motor.

3. Control-circuit transformer with primary and secondary side fuses.

C. Terminal blocks with numbered [and color-coded ]wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

Retain paragraph below to enclose wiring.  Chiller manufacturers do not normally enclose all wiring.  Consult manufacturer for availability.

D. Wiring Outside of Enclosures:  Factory installed in metal raceway except make terminal connections with not more than a 24-inch (610-mm) length of [liquidtight] [or] [flexible metallic] conduit.

2.15 CONTROLS

Coordinate this article with Division 23 Section "Instrumentation and Control for HVAC."

A. Control:  Standalone and microprocessor based, with all memory stored in nonvolatile memory so that reprogramming is not required on loss of electrical power.

B. Enclosure:  Unit mounted, NEMA 250, [Type 1] [Type 4] [Type 4x] <Insert type>, hinged or lockable.

C. Operator Interface:  Multiple-character digital or graphic display with dynamic update of information and with keypad or touch-sensitive display located on front of control enclosure.  In either imperial or metric units selectable through the interface, display the following information:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Date and time.

2. Operating or alarm status.

3. Operating hours.

4. Outdoor-air temperature if required for chilled-water reset.

5. Temperature and pressure of operating set points.

6. Entering and leaving temperatures of chilled and condenser water.

7. Refrigerant temperature.

8. Solution concentration and temperature.

9. Indication of solution and purge-pump operation.

10. Generator shell pressure.

11. Number of starts.

12. Number of purge cycles.

Retain first two subparagraphs below for chillers fed with hot water.

13. Hot-water valve actuator potentiometer position (percentage).

14. Entering and leaving hot-water temperatures.

Retain first three subparagraphs below for chillers fed with steam.

15. Steam demand limit.

16. Inlet steam pressure and temperature.

17. Steam valve actuator potentiometer position (percentage).

Retain first subparagraph below for double-effect chillers.

18. First-stage generator pressure and temperature.

19. <Insert status display items>.

D. Control Functions:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Manual or automatic startup and shutdown time schedule.

2. Automatic cycle to prevent crystallization.

3. Entering and leaving chilled-water temperatures and control set points.  Chilled-water temperature shall be reset based on [return-water] [outdoor-air] [space] temperature.

4. Condenser-fluid temperature.

LEED-NC Credit EA 5 requires measurement of performance according to International Performance Measurement and Verification Protocol.  If pursuing Credit EA 5, retain first subparagraph below along with satisfying other requirements.  See Evaluations.

5. Cooling provided and heating energy used within programmable time periods, minimum monthly.

6. <Insert control functions>.

E. Capacity Control:  Automatically controls input flow rate of heat source to maintain chilled-water temperature set point for cooling loads ranging from 10 to 100 percent.

F. Control Valve Package:  [Factory-furnished, for field installation,] [Factory-installed] control valve package suitable for energy source indicated.

1. Body:  Cast-iron, carbon-steel, or stainless-steel body with flanged connections.

2. Type:  [Manufacturer's choice] [V-notch ball] [Butterfly] [Globe style with cage-guide plug] <Insert type> constructed of stainless steel.

3. Rating:  Pressure and temperature rating to match heat exchanger.

4. Shutoff:  Capable of bubble-tight shutoff against maximum system pressure.

5. Size:  Determined by chiller manufacturer.

6. Modulation:  [Two] [Three]-way.

7. Turndown:  As required to achieve stable control through the indicated operating range.

8. Actuator:  Electric powered from chiller control panel and installed on valve.

G. Safety Shutdowns:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Crystallization.

2. Low refrigerant temperature.

3. Loss of chilled- or condenser-water flow.

4. Low leaving chilled-water temperature[, 2 deg F (1 deg C) below set point].

5. First-stage generator low-solution level.

6. First-stage generator high temperature or pressure.

7. Power failure.

8. Solution pump overloads.

9. External auxiliary safety shutdown.

10. High solution concentration.

11. Incomplete dilution cycle.

Retain first subparagraph below for chillers fed with hot water.

12. High entering-water temperature.

Retain first subparagraph below for chillers fed with steam.

13. High inlet steam pressure and temperature.

14. <Insert conditions>.

H. Warning Conditions:  Control panel shall close warning contacts and generate a message when one of the following operating conditions is detected:

Verify availability of requirements in subparagraphs below with manufacturers.

1. Low refrigerant temperature.

2. High generator temperature or pressure.

3. High entering generator-water temperature (single-stage generator only).

4. High or low entering condenser-water temperature.

5. Solution temperature sensor failure.

6. Low chilled-water flow.

7. <Insert warning conditions>.

I. Trending:  Capability to trend analog data of up to five parameters simultaneously over an adjustable period and frequency of polling.

J. Security Access:  Provide electronic security access to controls through identification and password with at least three levels of access:  view only; view and operate; and view, operate, and service.

K. Control Authority:  At least four conditions:  Off, local manual control at chiller, local automatic control at chiller, and automatic control through a remote source.

L. Communication Port:  RS-232 port, USB 2.0 port, or equivalent connection capable of connecting a printer[ and a notebook computer].

Retain paragraph below if chiller controls interface with the BAS.  Coordinate with Division 23 Section "Instrumentation and Control for HVAC."

M. BAS Interface:  Factory-installed hardware and software to enable the BAS to monitor, control, and display chiller status and alarms.

Retain first subparagraph below if interface with the BAS is through hardwired points and minimal interface is required.

1. Hardwired Points:

a. Monitoring:  On-off status, [common trouble alarm] <Insert monitoring point>.

b. Control:  On-off operation, [chilled-water, discharge temperature set-point adjustment] [generator heat source capacity limiting] <Insert control point>.

Delete "Hardwired Points" Subparagraph above and retain subparagraph below if extensive interface with the BAS is required and is beyond what hardwired points can provide.  Requirement may exclude some manufacturers.

2. [ASHRAE 135 (BACnet)] [LonTalk] [Modbus] [Industry-accepted, open-protocol] <Insert type of interface> communication interface with the BAS shall enable the BAS operator to remotely control and monitor the chiller from an operator workstation.  Control features and monitoring points displayed locally at chiller control panel shall be available through the BAS.

2.16 FINISH

A. Paint chiller, using manufacturer's standard procedures, except comply with the following minimum requirements:

1. Provide at least one coat of primer with a total dry film thickness of at least 2 mils (0.05 mm).

2. Provide at least two coats of [alkyd-modified, vinyl enamel] [epoxy] [polyurethane] finish with a total dry film thickness of at least 4 mils (0.10 mm).

3. Paint surfaces that are to be insulated before applying the insulation.

4. Paint installed insulation to match adjacent uninsulated surfaces.

5. Color of finish coat to be [manufacturer's standard] [custom color selected by Architect] <Insert color description>.

B. Provide Owner with quart container of paint used in application of topcoat to use in touchup applications after Project Closeout.

2.17 ACCESSORIES

A. Sight Glasses:  Equip unit with sight glasses for visual inspection of absorbent solution and refrigerant levels.  Provide at least one sight glass in absorber and evaporator sections.

Retain one or more paragraphs below to add features furnished by chiller manufacturer.

B. Flow Switches:

1. Chiller manufacturer shall furnish a switch for each [condenser] [evaporator and condenser] and verify field-mounting location before installation.

Retain one of two subparagraphs below.  Consult manufacturers for flow-switch requirements.

2. Paddle Flow Switches:

a. Vane operated to actuate a double-pole, double-throw switch with one pole field wired to the chiller control panel and the other pole field wired to the BAS.

b. Contacts:  Platinum alloy, silver alloy, or gold-plated switch contacts with a rating of 10 A at 120-V ac.

c. Pressure rating equal to pressure rating of heat exchanger.

d. Construct body and wetted parts of Type 316 stainless steel.

e. House switch in a NEMA 250, [Type 4] <Insert type> enclosure constructed of die-cast aluminum.

f. Vane length to suit installation.

3. Pressure Differential Switches:

a. Construction:  Wetted parts of body and trim constructed of Type 316 stainless steel.

b. Performance:  Switch shall withstand, without damage, the full-pressure rating of the heat exchanger applied to either port and exhibit zero set-point shift due to variation in working pressure.

c. Set Point:  Screw type, field adjustable.

d. Electrical Connections:  Internally mounted screw-type terminal blocks.

e. Switch Enclosure:  NEMA 250, [Type 4] <Insert type>.

f. Switch Action:  Double-pole, double-throw switch with one pole field wired to the chiller control panel and the other pole field wired to the BAS.

C. Vibration Isolation:

1. Chiller manufacturer shall furnish neoprene-pad vibration isolation for each chiller.

a. Two layers of 0.375-inch- (10-mm-) thick, ribbed- or waffle-pattern neoprene pads separated by a 16-gage, stainless-steel plate.

b. Fabricate pads from 40- to 50-durometer neoprene.

c. Provide stainless-steel square bearing plate to load the pad uniformly between 20 and 40 psig (138 and 276 kPa) with a 0.12- to 0.16-inch (3- to 4-mm) deflection.

Paragraph below is an optional feature specific to Trane's absorption chillers.  Consult other manufacturers for availability.

D. Lithium Bromide Filter:

1. Factory install a filter, isolation valves, and associated piping.

2. Filter shall consist of a stainless-steel body, with removable and cleanable 150-micron, stainless-steel element.

3. Isolation valves shall provide isolation for filter servicing without disturbing operation of chiller.

2.18 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of indirect-fired, absorption chillers, delete this article and schedule chillers on Drawings.

A. Capacity:  <Insert tons (kW)>.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

B. Full-Load Efficiency (COP):  <Insert number>.

Retain first option in first paragraph below if operating conditions reference ARI standard rating conditions; retain second option if operating conditions are other than ARI standard rating conditions.

C. Part-Load Efficiency [(IPLV)] [(NPLV)]:  <Insert number>.

D. Evaporator:

1. Pressure Rating:  [150 psig (1035 kPa)] [300 psig (2070 kPa)] <Insert psig (kPa)>.

2. Number of Passes:  [One] [Two] [Three] <Insert number>.

3. Fluid Type:  [Water] <Insert fluid type>.

4. Design Fluid Flow Rate:  <Insert gpm (L/s)>.

5. Minimum Fluid Flow Rate:  <Insert gpm (L/s)>.

6. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

7. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

8. Fluid Pressure Drop:  <Insert feet of head (kPa)>.

9. Fluid Velocity:  <Insert fps (m/s)>.

Fouling factor units in subparagraph below are consistent with ARI 560; first option is based on ARI 560 standard rating.

10. Fouling Factor:  [0.0001 sq. ft. x h x deg F/Btu (0.000018 sq. m x deg C/W)] [0.00025 sq. ft. x h x deg F/Btu (0.000045 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] <Insert value>.

E. Absorber/Condenser:

1. Pressure Rating:  [150 psig (1035 kPa)] [300 psig (2070 kPa)] <Insert psig (kPa)>.

2. Number of Passes:  [One] [Two] [Three].

3. Fluid Type:  [Water] <Insert fluid type>.

4. Design Fluid Flow Rate:  <Insert gpm (L/s)>.

5. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

6. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

7. Fluid Pressure Drop:  <Insert feet of head (kPa)>.

8. Fluid Velocity:  <Insert fps (m/s)>.

Fouling factor units in subparagraph below are consistent with ARI 560; first option is based on ARI 560 standard rating.

9. Fouling Factor:  [0.00025 sq. ft. x h x deg F/Btu (0.000045 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] [0.001 sq. ft. x h x deg F/Btu (0.00022 sq. m x deg C/W)] <Insert value>.

Retain first paragraph below for chillers fed from a hot-water source.

F. Hot-Water Generator:

1. Capacity:  <Insert MBtu/h (kW)>.

2. Pressure Rating:  [150 psig (1035 kPa)] [300 psig (2070 kPa)] <Insert psig (kPa)>.

3. Number of Passes:  [One] [Two] [Three].

4. Fluid Type:  [Water] <Insert fluid type>.

5. Design Fluid Flow Rate:  <Insert gpm (L/s)>.

6. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

7. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

8. Fluid Pressure Drop:  <Insert feet of head (kPa)>.

9. Fluid Velocity:  <Insert fps (m/s)>.

Fouling factor units in subparagraph below are consistent with ARI 560; first option is based on ARI 560 standard rating.

10. Fouling Factor:  [0.0001 sq. ft. x h x deg F/Btu (0.000018 sq. m x deg C/W)] [0.00025 sq. ft. x h x deg F/Btu (0.000045 sq. m x deg C/W)] [0.0005 sq. ft. x h x deg F/Btu (0.00011 sq. m x deg C/W)] <Insert value>.

Retain first paragraph below for chillers fed from a steam source.

G. Steam Generator:

1. Capacity:  <Insert MBtu/h (kW)>.

2. Flow Rate:  <Insert lb/h (L/s)>.

3. Pressure:  <Insert psig (kPa)>.

Retain first option in subparagraph below for single-effect chillers; retain second option for double-effect absorption chillers.

4. Pressure Rating:  [15 psig (104 kPa)] [150 psig (1035 kPa)] <Insert psig (kPa)>.

H. Pump Horsepower:

1. Purge:  <Insert value>.

2. Refrigerant:  <Insert value>.

3. Solution:  <Insert value>.

I. Chiller Control Electrical Requirements:

1. Power Input:  <Insert kilowatts>.

2. Minimum Circuit Ampacity:  <Insert value>.

3. Maximum Overcurrent Protection Device:  <Insert amperage>.

4. Characteristics:  [120] <Insert value>-V ac, single phase, 60 Hz.

J. Chiller Electrical Requirements:

1. Power Input:  <Insert kilowatts>.

2. Minimum Circuit Ampacity:  <Insert value>.

3. Maximum Overcurrent Protection Device:  <Insert amperage>.

4. Characteristics:  [208] [240] [480] <Insert value>-V ac, three phase, 60 Hz.

K. Noise Rating:  [80] [85] <Insert dBA> sound power level when measured according to ARI 575.  Provide factory-installed sound treatment if necessary to achieve the performance indicated.

2.19 HEAT-EXCHANGER, BRUSH-CLEANING SYSTEM

A. Furnish for field installation a brush-cleaning system on each chiller [condenser] <Insert heat exchanger> for tube cleaning and improved heat transfer.

B. System shall maintain tube fouling at or below design conditions without interrupting normal equipment operation.

C. System shall consist of a brush inserted in each tube and a catch basket attached to each end of the tube.  A four-way valve shall operate to reverse the direction of water flow to push the brush through the tube while removing tube deposits.  Four-way reversing valve's actuator shall be controlled by a preset time cycle that provides regular tube brushing during equipment operation.  Frequency of the brushing cycle shall be set up to match Project requirements.

D. Components:

1. Brush:  Each brush shall have nylon bristles, titanium wires, and polypropylene tips.  Brush interference fit with the ID of the tube shall not exceed 0.025 inch (0.6 mm).

2. Basket:  Single-piece polypropylene basket with neck OD to press fit inner diameter of tube.  Design shall provide for insertion of eddy current probe or removal of brushes without removing baskets from the valve.

3. Four-Way Valve:

a. Construct valve body of carbon steel with internal sealing parts of hard rubber and Type 304 stainless steel.

b. Configure valve with parallel flow connections to minimize field installation piping.

c. Construct to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, at a system working pressure equal to condenser.

d. Pipe connections shall be flanged.

e. Valve manufacturer to test and certify a maximum leakage rate of less than 0.05 percent of the design flow rate at operation conditions of maximum differential pressure.

f. Hydrostatically test to 1.5 times the design working pressure.

g. Design the valve to cause no more than 0.5-psig (3-kPa) pressure drop at design flow conditions.

h. Provide valve with valve-mounted indicating/warning light, which shall light before the valve begins rotation.

Retain one of first two subparagraphs below.

i. Valve Actuator:  Mount electric actuator to operate valve.

j. Valve Actuator:  Mount pneumatic piston-type actuator to operate valve.  Actuator shall be suitable for operation using field-supplied air pressure.

k. Position Switches:  Factory mount microswitches on the valve to indicate the complete turn of valve in both normal and reverse flow.

4. Control Panel:  Factory or field mount a control panel on chiller.  Control panel shall include the following features:

a. NEMA 250, [Type 1] [Type 4] [Type 4x] [Type 12] enclosure.

b. Timer to automatically initiate the cleaning cycle over a 24-hour period.

c. Manual override of preset cleaning cycle.

d. Visual indication of "Power On," "Diverter Position," "Normal Flow," "Reverse Flow," and "Valve Malfunction" indicating a slow turn or incomplete valve turn.

e. For pneumatic actuators, mount four-way solenoid valve for actuator operation in the control panel.

f. Flow-switch bypass.

g. Unloading signal to chiller.

2.20 SOURCE QUALITY CONTROL

Not all manufacturers "run test" chillers.  Consult manufacturers for availability.

Retain first paragraph below if required.  Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

A. Perform functional [run ]tests of chillers before shipping.

B. Factory test and inspect absorber, generator, evaporator and condenser according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.  Pressure test tube-side of heat exchangers, including water boxes, to 1.5 times the rated pressure.  Vacuum and pressure test shells for leaks.

C. Rate sound power level according to ARI 575.

Retain first paragraph below for factory performance testing.  Factory performance tests are an added cost.  Verify requirement with Owner.

D. Factory performance test chillers, before shipping, according to ARI 560.

1. Test the following conditions:

a. Design conditions indicated.

Retain one of three subparagraphs below for part-load performance testing.

b. Reduction in capacity from design to minimum load in steps of [10] [25] [33] <Insert number> with condenser fluid at design conditions.

c. Reduction in capacity from design to minimum load in steps of [10] [25] [33] <Insert number> with varying entering condenser-fluid temperature from design to minimum conditions in [5 deg F (3 deg C)] <Insert temperature> increments.

d. At [one] [two] [three] [four] [five] [10] <Insert number> point(s) of varying part-load performance to be selected by Owner at time of test.

Retain first paragraph below for factory sound testing.  Factory sound tests are an added cost and may not be available from some manufacturers.  Verify requirement with Owner.

E. Factory sound test chillers, before shipping, according to ARI 575.

1. Test the following conditions:

a. Design conditions indicated.

b. Chiller operating at calculated worst-case sound condition.

c. At [one] [two] [three] [four] [five] <Insert number> point(s) of varying part-load performance to be selected by Owner at time of test.

Retain first paragraph below to witness testing.

F. Allow [Owner] <Insert entity> access to place where chillers are being tested.  Notify Architect [14] <Insert number> days in advance of testing.

G. Prepare test report indicating test procedures, instrumentation, test conditions, and results.  Submit copy of results within one week of test date.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine chillers before installation.  Reject chillers that are damaged.

B. Examine roughing-in for equipment support, anchor-bolt sizes and locations, piping, and electrical connections to verify actual locations, sizes, and other conditions affecting chiller performance, maintenance, and operations before equipment installation.

1. Final chiller locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 CHILLER INSTALLATION

Retain first paragraph below if chillers are to be installed on a support structure other than a concrete base.  Indicate design of support structure on Drawings.

A. Install chillers on support structure indicated.

Retain one of first three paragraphs below.  If retaining more than one, show mounting type on Drawings.  Coordinate with Drawings and Sections specifying vibration and seismic controls.  Retain or insert amount of required deflection.

Retain first paragraph below for equipment supported on concrete bases and vibration isolation devices.

B. Equipment Mounting:  Install chiller on concrete bases using [elastomeric pads] <Insert device>.  Comply with requirements for concrete bases specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]." Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1/2 inch (13 mm)] <Insert dimension>.

2. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

3. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

4. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

5. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below for equipment supported on vibration isolation devices without a concrete base.

C. Equipment Mounting:  Install chiller using [elastomeric pads] <Insert device>.  Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1/2 inch (13 mm)] <Insert dimension>.

Retain first paragraph below for equipment installed on concrete bases without vibration isolation devices.  This may be appropriate for chillers on structural slabs-on-grade.

D. Equipment Mounting:  Install chiller on concrete bases.  Comply with requirements for concrete bases specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below for installation of equipment without vibration isolation devices, with seismic restraints, and without concrete base.

E. Install chillers with seismic-restraint device.  Comply with requirements for seismic-restraint devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Retain first paragraph below if piping is required to withstand seismic design loads.

F. Install seismic restraints on piping.  Comply with requirements for seismic-restraint devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

G. Maintain manufacturer's recommended clearances for service and maintenance.

H. Charge chiller with absorbent and refrigerant if not factory charged.

I. Install separate devices furnished by manufacturer and not factory installed.

J. Insulate hot and cold chiller surfaces that are recommended by chiller manufacturer to be insulated, and are not factory insulated.  Comply with requirements in Division 23 Section "HVAC Insulation."

3.3 HEAT-EXCHANGER, BRUSH-CLEANING SYSTEM INSTALLATION

Retain this article for heat-exchanger, brush-cleaning system.  Coordinate with "Heat-Exchanger, Brush-Cleaning System" Article.

A. Install brush-cleaning system control panel adjacent to chiller control panel.

B. Arrange piping to provide service access to four-way valve assembly without affecting access to chiller.  Secure valve to prevent lateral movement and vibration during operation.

C. Provide field electric power, as required, to each system control panel and electric actuated valve.

D. Provide pneumatic piping with pressure regulator and isolation valve to each pneumatic supply connection.  Coordinate field source of air with manufacturer to ensure that requirements are satisfied for proper valve operation.

E. Interconnect brush-cleaning system controls with chiller controls.  Coordinate requirements to ensure safe, trouble-free operation.

F. Functionally test the entire brush-cleaning system, including the valve, actuator, position indicator, and control panel, with chiller in operation.

3.4 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in Division 23 Sections "Hydronic Piping" and "Steam and Condensate Heating Piping." If Drawings are explicit enough, these requirements may be reduced or omitted.

If using hot water as a heating source, confirm the water temperature used on Project is within the applicable temperature range of the other Sections referenced.  Otherwise, revise Sections to suit Project requirements.  This is of concern if water temperature is above 250 deg F (121 deg C).

A. Comply with requirements in Division 23 Section "Hydronic Piping" for hydronic piping.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Comply with requirements in Division 23 Section "Steam and Condensate Heating Piping" for steam and condensate piping.  Drawings indicate general arrangement of piping, fittings, and specialties.

C. Install piping adjacent to chiller to allow service and maintenance.

Retain first paragraph below for chillers fed from a steam source.

D. Generator Steam Piping Connections:

1. Connect steam piping with trapped drip leg, gate valve, strainer, control valve, and pressure gage.  Install pressure reducing valve and safety relief valve upstream from steam-control valve to protect control valve from excessive steam pressure.  Make connections to chiller with a [flange] [or] [union].

2. Connect steam condensate piping with vacuum breaker, trapped drip leg, gate valve, strainer, float and thermostatic trap(s), [condensate cooler,] [condensate receiver,] [condensate receiver and pump,] and check valve.  Make connections to chiller with a [flange] [or] [union].

Retain first paragraph below for chillers fed from a hot-water source.

E. Generator Hot-Water Connections:  Connect to generator inlet with shutoff valve, [strainer,] [flexible connector,] control valve, thermometer, and plugged tee with shutoff valve and pressure gage.  Connect to generator outlet with shutoff valve, check valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with shutoff valve and pressure gage,[ flow meter,] and drain connection with valve.  Make connections to chiller with a [flange] [or] [mechanical coupling].

F. Evaporator-Fluid Connections:  Connect to evaporator inlet with shutoff valve, [strainer,] [flexible connector,] thermometer, and plugged tee with shutoff valve and pressure gage.  Connect to evaporator outlet with shutoff valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with shutoff valve and pressure gage,[ flow meter,] and drain connection with valve.  Make connections to chiller with a [flange] [or] [mechanical coupling].

G. Absorber/Condenser-Fluid Connections:  Connect to inlet with shutoff valve, [strainer,] [flexible connector,] thermometer, and plugged tee with shutoff valve and pressure gage.  Connect to outlet with shutoff valve, balancing valve,[ flexible connector,] flow switch, thermometer, plugged tee with shutoff valve and pressure gage,[ flow meter,] and drain connection with valve.  Make connections to chiller with a [flange] [or] [mechanical coupling].

1. If not factory furnished or installed, provide pipe connecting fluid connection of absorber discharge and condenser inlet.

H. Refrigerant Pressure Relief Device Connections:  Extend [vent piping] [separate vent piping for each chiller] to the outdoors without valves or restrictions.  Comply with ASHRAE 15.  Connect to chiller pressure relief device with flexible connector and dirt leg with drain valve.

I. Extend [purge vent piping] [separate purge vent piping for each chiller] to the outdoors.  Comply with ASHRAE 15.

J. Connect each chiller drain connection with a union and drain pipe, and extend pipe, full size of connection, to floor drain.  Provide a shutoff valve at each connection.

3.5 STARTUP SERVICE

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Operate chiller for run-in period.

3. Verify that absorbent and refrigerant charge is sufficient and chiller has been leak tested.

4. Verify that pumps are installed and functional.

5. Verify that thermometers and gages are installed.

6. Operate chiller for run-in period.

7. Verify that refrigerant pressure relief device is vented outside.

8. Verify proper motor rotation.

9. Verify static deflection of vibration isolators including deflection during chiller startup and shutdown.

10. Verify and record performance of fluid flow and low-temperature interlocks for evaporator and condenser.

11. Verify and record performance of chiller protection devices.

12. Test and adjust controls and safeties.  Replace damaged or malfunctioning controls and equipment.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assembly, installation, and connection.

C. Prepare test and inspection startup reports.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain chillers.[  Video record the training sessions.]

END OF SECTION 236413.16

	INDIRECT-FIRED ABSORPTION WATER CHILLERS
	236413.16 - 1



