Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
06/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260533 - RACEWAY AND BOXES FOR ELECTRICAL SYSTEMS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes raceways, fittings, boxes, enclosures, and cabinets for electrical wiring.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

Retain subparagraph below for underground conduits, handholes, and boxes; delete if incidental exterior underground raceways, handholes, and boxes are specified in this Section.

1. Division 26 Section "Underground Ducts and Raceways for Electrical Systems" for exterior ductbanks, manholes, and underground utility construction.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. EMT:  Electrical metallic tubing.

B. ENT:  Electrical nonmetallic tubing.

C. EPDM:  Ethylene-propylene-diene terpolymer rubber.

D. FMC:  Flexible metal conduit.

E. IMC:  Intermediate metal conduit.

F. LFMC:  Liquidtight flexible metal conduit.

G. LFNC:  Liquidtight flexible nonmetallic conduit.

H. NBR:  Acrylonitrile-butadiene rubber.

I. RNC:  Rigid nonmetallic conduit.

1.4 SUBMITTALS

A. Product Data:  For surface raceways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.

B. Shop Drawings:  For the following raceway components.  Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph below for custom enclosures only.

1. Custom enclosures and cabinets.

Retain subparagraph and associated subparagraphs below if handholes or boxes for underground wiring are specified; delete if these raceway components are specified in Division 26 Section "Underground Ducts and Raceways for Electrical Systems."

2. For handholes and boxes for underground wiring, including the following:

a. Duct entry provisions, including locations and duct sizes.

b. Frame and cover design.

c. Grounding details.

d. Dimensioned locations of cable rack inserts, and pulling-in and lifting irons.

e. Joint details.

Retain sample requirements in two paragraphs below if Architect wants to select colors.  Delete first paragraph and subparagraph if colors are preselected and specified or scheduled.

C. Samples for Initial Selection:  For [wireways] [nonmetallic wireways] [and] [surface raceways] with factory-applied texture and color finishes.

1. Size:  <Insert sample size.>

D. Samples for Verification:  For each type of exposed finish required for [wireways] [nonmetallic wireways] [and] [surface raceways], prepared on Samples of size indicated below.

1. Size:  <Insert sample size.>

Retain paragraph and subparagraphs below if Drawings do not include detailed conduit routing plans and if Project involves unusual coordination requirements.

E. Coordination Drawings:  Conduit routing plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Structural members in the paths of conduit groups with common supports.

2. HVAC and plumbing items and architectural features in the paths of conduit groups with common supports.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

F. Manufacturer Seismic Qualification Certification:  Submit certification that enclosures and cabinets and their mounting provisions, including those for internal components, will withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain option in first subparagraph below for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the cabinet or enclosure will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will retain its enclosure characteristics, including its interior accessibility, after the seismic event]."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if nonconcrete handholes or boxes are specified and testing is specified in Part 2 "Source Quality Control for Underground Enclosures" Article.

G. Qualification Data:  For professional engineer and testing agency.

H. Source quality-control test reports.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 METAL CONDUIT AND TUBING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. AFC Cable Systems, Inc.

2. Alflex Inc.

3. Allied Tube & Conduit; a Tyco International Ltd. Co.

4. Anamet Electrical, Inc.; Anaconda Metal Hose.

5. Electri-Flex Co.

6. Manhattan/CDT/Cole-Flex.

7. Maverick Tube Corporation.

8. O-Z Gedney; a unit of General Signal.

9. Wheatland Tube Company.

10. <Insert manufacturer's name.>

C. Rigid Steel Conduit:  ANSI C80.1.

Retain first paragraph below for corrosion-resistant power distribution at frequencies above 60 Hz or for other special conditions.

D. Aluminum Rigid Conduit:  ANSI C80.5.

E. IMC:  ANSI C80.6.

F. PVC-Coated Steel Conduit:  PVC-coated [rigid steel conduit] [IMC].

1. Comply with NEMA RN 1.

2. Coating Thickness:  0.040 inch (1 mm), minimum.

G. EMT:  ANSI C80.3.

In first paragraph below, zinc-coated steel is most common type.  Retain second option to allow Contractor to choose material.

H. FMC:  [Zinc-coated steel][ or aluminum].

I. LFMC:  Flexible steel conduit with PVC jacket.

J. Fittings for Conduit (Including all Types and Flexible and Liquidtight), EMT, and Cable:  NEMA FB 1; listed for type and size raceway with which used, and for application and environment in which installed.

Coordinate first subparagraph below with Drawings.

1. Conduit Fittings for Hazardous (Classified) Locations:  Comply with UL 886.

2. Fittings for EMT:  [Steel] [Die-cast] [Steel or die-cast], [set-screw] [compression] [set-screw or compression] type.

3. Coating for Fittings for PVC-Coated Conduit:  Minimum thickness, 0.040 inch (1 mm), with overlapping sleeves protecting threaded joints.

Retain paragraph below to require some threaded joints of rigid steel conduit or IMC, or their fittings, to be treated with joint compound for improved conductivity, resistance to oxidation, or ease of assembly and disassembly.

K. Joint Compound for Rigid Steel Conduit or IMC:  Listed for use in cable connector assemblies, and compounded for use to lubricate and protect threaded raceway joints from corrosion and enhance their conductivity.

2.2 NONMETALLIC CONDUIT AND TUBING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. AFC Cable Systems, Inc.

2. Anamet Electrical, Inc.; Anaconda Metal Hose.

3. Arnco Corporation.

4. CANTEX Inc.

5. CertainTeed Corp.; Pipe & Plastics Group.

6. Condux International, Inc.

7. ElecSYS, Inc.

8. Electri-Flex Co.

9. Lamson & Sessions; Carlon Electrical Products.

10. Manhattan/CDT/Cole-Flex.

11. RACO; a Hubbell Company.

12. Thomas & Betts Corporation.

13. <Insert manufacturer's name.>

See Evaluations for descriptions of nonmetallic conduit types.

C. ENT:  NEMA TC 13.

D. RNC:  NEMA TC 2, [Type EPC-40-PVC, ]unless otherwise indicated.

E. LFNC:  UL 1660.

F. Fittings for ENT and RNC:  NEMA TC 3; match to conduit or tubing type and material.

G. Fittings for LFNC:  UL 514B.

2.3 OPTICAL FIBER/COMMUNICATIONS CABLE RACEWAY AND FITTINGS

Retain this Article to specify special-purpose, flexible nonmetallic raceways permitted by NFPA 70, "Optical Fiber Cables and Raceways" and "Communications Circuits" articles.  See Evaluations.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Arnco Corporation.

2. Endot Industries Inc.

3. IPEX Inc.

4. Lamson & Sessions; Carlon Electrical Products.

C. Description:  Comply with UL 2024; flexible type, approved for [plenum] [riser] [general-use] installation.

2.4 METAL WIREWAYS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Cooper B-Line, Inc.

2. Hoffman.

3. Square D; Schneider Electric.

4. <Insert manufacturer's name.>

C. Description:  Sheet metal sized and shaped as indicated, NEMA 250, Type [1] [12] [3R], unless otherwise indicated.

D. Fittings and Accessories:  Include couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for complete system.

E. Wireway Covers:  [Hinged type] [Screw-cover type] [Flanged-and-gasketed type] [As indicated].

F. Finish:  Manufacturer's standard enamel finish.

2.5 NONMETALLIC WIREWAYS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Hoffman.

2. Lamson & Sessions; Carlon Electrical Products.

3. <Insert manufacturer's name.>

Retain one of first two paragraphs below.

C. Description:  Fiberglass polyester, extruded and fabricated to size and shape indicated, with no holes or knockouts.  Cover is gasketed with oil-resistant gasket material and fastened with captive screws treated for corrosion resistance.  Connections are flanged, with stainless-steel screws and oil-resistant gaskets.

D. Description:  PVC plastic, extruded and fabricated to size and shape indicated, with snap-on cover and mechanically coupled connections with plastic fasteners.

E. Fittings and Accessories:  Include couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for complete system.

2.6 SURFACE RACEWAYS

Insert requirements for finish-coat paint color, if applicable, in first paragraph below.  See Division 09 for optional field-finish coats.

A. Surface Metal Raceways:  Galvanized steel with snap-on covers.  [Manufacturer's standard enamel finish in color selected by Architect] [Prime coating, ready for field painting].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Thomas & Betts Corporation.

b. Walker Systems, Inc.; Wiremold Company (The).

c. Wiremold Company (The); Electrical Sales Division.

d. <Insert manufacturer's name.>

B. Surface Nonmetallic Raceways:  Two-piece construction, manufactured of rigid PVC with texture and color selected by Architect from [manufacturer's standard] [custom] colors.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Butler Manufacturing Company; Walker Division.

b. Enduro Systems, Inc.; Composite Products Division.

c. Hubbell Incorporated; Wiring Device-Kellems Division.

d. Lamson & Sessions; Carlon Electrical Products.

e. Panduit Corp.

f. Walker Systems, Inc.; Wiremold Company (The).

g. Wiremold Company (The); Electrical Sales Division.

h. <Insert manufacturer's name.>

2.7 BOXES, ENCLOSURES, AND CABINETS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Cooper Crouse-Hinds; Div. of Cooper Industries, Inc.

2. EGS/Appleton Electric.

3. Erickson Electrical Equipment Company.

4. Hoffman.

5. Hubbell Incorporated; Killark Electric Manufacturing Co. Division.

6. O-Z/Gedney; a unit of General Signal.

7. RACO; a Hubbell Company.

8. Robroy Industries, Inc.; Enclosure Division.

9. Scott Fetzer Co.; Adalet Division.

10. Spring City Electrical Manufacturing Company.

11. Thomas & Betts Corporation.

12. Walker Systems, Inc.; Wiremold Company (The).

13. Woodhead, Daniel Company; Woodhead Industries, Inc. Subsidiary.

14. <Insert manufacturer's name.>

C. Sheet Metal Outlet and Device Boxes:  NEMA OS 1.

In first paragraph below, aluminum boxes are suitable for use with steel raceways in most environments.  Type FD is a device box with extra depth.  Many other configurations are available.

D. Cast-Metal Outlet and Device Boxes:  NEMA FB 1, [ferrous alloy] [aluminum], Type FD, with gasketed cover.

E. Nonmetallic Outlet and Device Boxes:  NEMA OS 2.

See Editing Instruction No. 2 in the Evaluations for a discussion of floor boxes.

F. Metal Floor Boxes:  [Cast metal] [Sheet metal] [Cast or sheet metal], [fully adjustable] [semi-adjustable], rectangular.

G. Nonmetallic Floor Boxes:  Nonadjustable, round.

H. Small Sheet Metal Pull and Junction Boxes:  NEMA OS 1.

I. Cast-Metal Access, Pull, and Junction Boxes:  NEMA FB 1, [cast aluminum] [galvanized, cast iron] with gasketed cover.

Coordinate first paragraph and subparagraphs below with Drawings if hinged cover enclosures other than NEMA 250, Type 1 are required, e.g., very dusty areas, and if consideration should be given to use of NEMA 250, Type 12 enclosures.

J. Hinged-Cover Enclosures:  NEMA 250, Type 1, with continuous-hinge cover with flush latch, unless otherwise indicated.

1. Metal Enclosures:  Steel, finished inside and out with manufacturer's standard enamel.

2. Nonmetallic Enclosures:  Plastic[, finished inside with radio-frequency-resistant paint].

K. Cabinets:

1. NEMA 250, Type 1, galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

2. Hinged door in front cover with flush latch and concealed hinge.

3. Key latch to match panelboards.

4. Metal barriers to separate wiring of different systems and voltage.

5. Accessory feet where required for freestanding equipment.

2.8 HANDHOLES AND BOXES FOR EXTERIOR UNDERGROUND WIRING

See Editing Instruction No. 3 in the Evaluations.  Verify with manufacturers that units of types specified are available in sizes required.  Indicate the size of each enclosure on Drawings, and use a symbol or other notation to differentiate between handholes and pull boxes.

A. Description:  Comply with SCTE 77.

1. Color of Frame and Cover:  [Gray] [Green].

First option in first subparagraph below facilitates bottom conduit entry.  Second option may be provided by a separate slab placed in the excavation under an open-bottom enclosure; third option is obtained by molding or fabricating the bottom integrally with the body of unit.

2. Configuration:  Units shall be designed for flush burial and have [open] [closed] [integral closed] bottom, unless otherwise indicated.

3. Cover:  Weatherproof, secured by tamper-resistant locking devices and having structural load rating consistent with enclosure.

4. Cover Finish:  Nonskid finish shall have a minimum coefficient of friction of 0.50.

5. Cover Legend:  Molded lettering, ["ELECTRIC." ] ["TELEPHONE." ] [as indicated for each service.] <Insert legend.>

Retain first subparagraph below if conduit will enter enclosure through the side.  Otherwise, entry will be made through an open bottom or through side openings cut in the field, as specified in Part 3.  Coordinate with Drawings.

6. Conduit Entrance Provisions:  Conduit-terminating fittings shall mate with entering ducts for secure, fixed installation in enclosure wall.

7. Handholes [12 inches wide by 24 inches long (300 mm wide by 600 mm long)] <Insert dimensions> and larger shall have inserts for cable racks and pulling-in irons installed before concrete is poured.

Retain one or more of three paragraphs and associated subparagraphs below to select enclosure type(s) for areas not subject to traffic by vehicles.  Coordinate selection with Part 3 "Raceway Application" Article.  For enclosures with cover options, verify that selected cover is available with load rating specified in Part 3 "Raceway Application" Article, subparagraph "Application of Handholes and Boxes for Underground Wiring."

B. Polymer-Concrete Handholes and Boxes with Polymer-Concrete Cover:  Molded of sand and aggregate, bound together with polymer resin, and reinforced with steel or fiberglass or a combination of the two.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armorcast Products Company.

b. Carson Industries LLC.

c. CDR Systems Corporation.

d. NewBasis.

e. <Insert manufacturer's name.>

C. Fiberglass Handholes and Boxes with Polymer-Concrete Frame and Cover:  Sheet-molded, fiberglass-reinforced, polyester-resin enclosure joined to polymer-concrete top ring or frame.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Armorcast Products Company.

b. Carson Industries LLC.

c. Christy Concrete Products.

d. Synertech Moulded Products, Inc.; a division of Oldcastle Precast.

e. <Insert manufacturer's name.>

D. Fiberglass Handholes and Boxes:  Molded of fiberglass-reinforced polyester resin, with covers of [polymer concrete] [reinforced concrete] [cast iron] [hot-dip galvanized-steel diamond plate] [fiberglass].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Carson Industries LLC.

b. Christy Concrete Products.

c. Nordic Fiberglass, Inc.

d. <Insert manufacturer's name.>

2.9 SLEEVES FOR RACEWAYS

A. Steel Pipe Sleeves:  ASTM A 53/A 53M, Type E, Grade B, Schedule 40, galvanized steel, plain ends.

Consider retaining first paragraph below if cables penetrate exterior walls below grade.

B. Cast-Iron Pipe Sleeves:  Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop, unless otherwise indicated.

C. Sleeves for Rectangular Openings:  Galvanized sheet steel with minimum 0.052- or 0.138-inch (1.3- or 3.5-mm) thickness as indicated and of length to suit application.

D. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 07 Section "Penetration Firestopping."

2.10 SLEEVE SEALS

Retain this Article if annular space between pipe sleeves and raceways must be sealed against hydrostatic pressure.  Sleeve seals are usually furnished with EPDM sealing elements, plastic pressure plates, and carbon-steel bolts.  NBR and silicone sealing elements, carbon- and stainless-steel pressure plates, and stainless-steel bolts are available for special applications.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Advance Products & Systems, Inc.

2. Calpico, Inc.

3. Metraflex Co.

4. Pipeline Seal and Insulator, Inc.

5. <Insert manufacturer's name.>

D. Description:  Modular sealing device, designed for field assembly, to fill annular space between sleeve and cable.

1. Sealing Elements:  [EPDM] [NBR] <Insert sealing element> interlocking links shaped to fit surface of cable or conduit.  Include type and number required for material and size of raceway or cable.

2. Pressure Plates:  [Plastic] [Carbon steel] [Stainless steel].  Include two for each sealing element.

3. Connecting Bolts and Nuts:  [Carbon steel with corrosion-resistant coating] [Stainless steel] of length required to secure pressure plates to sealing elements.  Include one for each sealing element.

2.11 SOURCE QUALITY CONTROL FOR UNDERGROUND ENCLOSURES

Retain this Article for underground handholes and pull boxes.  Delete if handholes and pull boxes are specified in Division 26 Section "Underground Ducts and Raceways for Electrical Systems."  See Evaluations.

A. Handhole and Pull-Box Prototype Test:  Test prototypes of handholes and boxes for compliance with SCTE 77.  Strength tests shall be for specified tier ratings of products supplied.

Retain one of first two subparagraphs below; retain first subparagraph to require an independent testing agency to test for compliance with SCTE requirements; retain second subparagraph to require testing by manufacturers' laboratories.  See Evaluations for a discussion about testing.

1. Tests of materials shall be performed by a independent testing agency.

2. Strength tests of complete boxes and covers shall be by either an independent testing agency or manufacturer.  A qualified registered professional engineer shall certify tests by manufacturer.

3. Testing machine pressure gages shall have current calibration certification complying with ISO 9000 and ISO 10012, and traceable to NIST standards.

PART 3 -  EXECUTION

3.1 RACEWAY APPLICATION

Retain this Article to specify type of raceway to be installed.  Coordinate with conductor and cable wiring methods specified in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables" and in other Sections in Divisions 26, 27, and 28. Do not duplicate information indicated on Drawings, required by NFPA 70, or specified in other Sections in Divisions 26, 27, and 28. Specify exceptions to requirements.  Verify requirements with authorities having jurisdiction to avoid specifying uses not permitted.  See "Writing Guide" Article in the Evaluations for instructions on editing this Article.

A. Outdoors:  Apply raceway products as specified below, unless otherwise indicated:

1. Exposed Conduit:  [Rigid steel conduit] [IMC] [RNC, Type EPC-40-PVC] [RNC, Type EPC-80-PVC].

2. Concealed Conduit, Aboveground:  [Rigid steel conduit] [IMC] [EMT] [RNC, Type EPC-40-PVC].

Retain subparagraph below if Project includes small amounts of exterior underground wiring, 600 V and less, and Division 26 Section "Underground Ducts and Raceways for Electrical Systems" is not being used.

3. Underground Conduit:  RNC, Type EPC-[40] [80]-PVC, direct buried.

Select first option in first subparagraph below if raceway may be exposed to physical damage.

4. Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment):  [LFMC] [LFNC].

5. Boxes and Enclosures, Aboveground:  NEMA 250, Type [3R] [4].

Retain subparagraph and associated subparagraphs below to specify types and structural load ratings of handholes and pull boxes.  See Editing Instruction No. 3 in the Evaluations.

6. Application of Handholes and Boxes for Underground Wiring:

a. Handholes and Pull Boxes in Driveway, Parking Lot, and Off-Roadway Locations, Subject to Occasional, Nondeliberate Loading by Heavy Vehicles:  [Polymer concrete] [Fiberglass enclosures with polymer-concrete frame and cover] [Fiberglass-reinforced polyester resin], SCTE 77, Tier 15 structural load rating.

b. Handholes and Pull Boxes in Sidewalk and Similar Applications with a Safety Factor for Nondeliberate Loading by Vehicles:  [Polymer-concrete units] [Heavy-duty fiberglass units with polymer-concrete frame and cover], SCTE 77, Tier 8 structural load rating.

c. Handholes and Pull Boxes Subject to Light-Duty Pedestrian Traffic Only:  Fiberglass-reinforced polyester resin, structurally tested according to SCTE 77 with 3000-lbf (13 345-N) vertical loading.

B. Comply with the following indoor applications, unless otherwise indicated:

1. Exposed, Not Subject to Physical Damage:  [EMT] [ENT] [or] [RNC].

2. Exposed, Not Subject to Severe Physical Damage:  [EMT] [RNC identified for such use].

3. Exposed and Subject to Severe Physical Damage:  [Rigid steel conduit] [IMC].  Includes raceways in the following locations:

a. Loading dock.

b. Corridors used for traffic of mechanized carts, forklifts, and pallet-handling units.

c. Mechanical rooms.

d. <Insert designations of applicable spaces or locations.>

4. Concealed in Ceilings and Interior Walls and Partitions:  [EMT] [ENT] [or] [RNC, Type EPC-40-PVC].

5. Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment):  FMC, except use LFMC in damp or wet locations.

6. Damp or Wet Locations:  [Rigid steel conduit] [IMC].

7. Raceways for Optical Fiber or Communications Cable in Spaces Used for Environmental Air:  [Plenum-type, optical fiber/communications cable raceway] [EMT] <Insert raceway type>.

8. Raceways for Optical Fiber or Communications Cable Risers in Vertical Shafts:  [Riser-type, optical fiber/communications cable raceway] [EMT] <Insert raceway type>.

9. Raceways for Concealed General Purpose Distribution of Optical Fiber or Communications Cable:  [General-use, optical fiber/communications cable raceway] [Riser-type, optical fiber/communications cable raceway] [Plenum-type, optical fiber/communications cable raceway] [EMT] <Insert raceway type>.

10. Boxes and Enclosures:  NEMA 250, Type 1, except use NEMA 250, Type 4, [stainless steel] [nonmetallic] in damp or wet locations.

C. Minimum Raceway Size:  [1/2-inch (16-mm)] [3/4-inch (21-mm)] trade size.

D. Raceway Fittings:  Compatible with raceways and suitable for use and location.

1. Rigid and Intermediate Steel Conduit:  Use threaded rigid steel conduit fittings, unless otherwise indicated.

2. PVC Externally Coated, Rigid Steel Conduits:  Use only fittings listed for use with that material.  Patch and seal all joints, nicks, and scrapes in PVC coating after installing conduits and fittings.  Use sealant recommended by fitting manufacturer.

Retain first paragraph below for high-frequency installation.

E. Install nonferrous conduit or tubing for circuits operating above 60 Hz.  Where aluminum raceways are installed for such circuits and pass through concrete, install in nonmetallic sleeve.

F. Do not install aluminum conduits in contact with concrete.

3.2 INSTALLATION

A. Comply with NECA 1 for installation requirements applicable to products specified in Part 2 except where requirements on Drawings or in this Article are stricter.

B. Keep raceways at least 6 inches (150 mm) away from parallel runs of flues and steam or hot-water pipes.  Install horizontal raceway runs above water and steam piping.

C. Complete raceway installation before starting conductor installation.

D. Support raceways as specified in Division 26 Section "Hangers and Supports for Electrical Systems."

E. Arrange stub-ups so curved portions of bends are not visible above the finished slab.

First paragraph below is more restrictive than NFPA 70, which permits up to four quarter bends in a conduit run.  Retain below for more conservative design, with less stress being placed on wire being pulled in.

F. Install no more than the equivalent of three 90-degree bends in any conduit run except for communications conduits, for which fewer bends are allowed.

G. Conceal conduit and EMT within finished walls, ceilings, and floors, unless otherwise indicated.

H. Raceways Embedded in Slabs:

1. Run conduit larger than 1-inch (27-mm) trade size, parallel or at right angles to main reinforcement.  Where at right angles to reinforcement, place conduit close to slab support.

2. Arrange raceways to cross building expansion joints at right angles with expansion fittings.

Note that some building or local electrical codes may not permit nonmetallic tubing in fire-rated slabs in subparagraph below.

3. Change from ENT to RNC, Type EPC-40-PVC, rigid steel conduit, or IMC before rising above the floor.

Retain paragraph below to require application of protective joint compound to threads of rigid steel conduit or IMC, and their fittings, where these raceways are installed outdoors or in wet, damp, or corrosive conditions.  This optional requirement exceeds NFPA70 rules.  If retaining, coordinate with Part 2 "Joint Compound for Rigid Steel Conduit or IMC" Paragraph and with Drawings indicating wet, damp, or corrosive indoor locations.

I. Threaded Conduit Joints, Exposed to Wet, Damp, Corrosive, or Outdoor Conditions:  Apply listed compound to threads of raceway and fittings before making up joints.  Follow compound manufacturer's written instructions.

Retain first paragraph below to exceed NFPA 70 requirements.  NFPA 70 requires insulated bushings or other smooth rounded entry provisions for conduit terminations at all locations where conductors are No. 4 AWG and larger, regardless of the environment.

J. Raceway Terminations at Locations Subject to Moisture or Vibration:  Use insulating bushings to protect conductors, including conductors smaller than No. 4 AWG.

K. Install pull wires in empty raceways.  Use polypropylene or monofilament plastic line with not less than 200-lb (90-kg) tensile strength.  Leave at least 12 inches (300 mm) of slack at each end of pull wire.

Paragraph below is applicable for EMT, ENT, FMC, IMC, RMC, RNC, and optical fiber/communications cable raceways.

L. Raceways for Optical Fiber and Communications Cable:  Install raceways, metallic and nonmetallic, rigid and flexible, as follows:

1. 3/4-Inch (19-mm) Trade Size and Smaller:  Install raceways in maximum lengths of 50 feet (15 m).

2. 1-Inch (25-mm) Trade Size and Larger:  Install raceways in maximum lengths of 75 feet (23 m).

3. Install with a maximum of two 90-degree bends or equivalent for each length of raceway unless Drawings show stricter requirements.  Separate lengths with pull or junction boxes or terminations at distribution frames or cabinets where necessary to comply with these requirements.

Retain paragraph and subparagraphs below if applicable.

M. Install raceway sealing fittings at suitable, approved, and accessible locations and fill them with listed sealing compound.  For concealed raceways, install each fitting in a flush steel box with a blank cover plate having a finish similar to that of adjacent plates or surfaces.  Install raceway sealing fittings at the following points:

1. Where conduits pass from warm to cold locations, such as boundaries of refrigerated spaces.

2. Where otherwise required by NFPA 70.

Retain paragraph and subparagraphs below unless locations for expansion fittings for PVC conduits are indicated on Drawings.  See Evaluations.

N. Expansion-Joint Fittings for RNC:  Install in each run of aboveground conduit that is located where environmental temperature change may exceed 30 deg F (17 deg C), and that has straight-run length that exceeds 25 feet (7.6 m).

1. Install expansion-joint fittings for each of the following locations, and provide type and quantity of fittings that accommodate temperature change listed for location:

Edit list below to include all locations in Project with environmental conditions that require considering expansion-joint fittings in PVC conduit runs.  For each Project, consider only locations with PVC conduit with straight-run length exceeding 25 feet (7.6 m).  Also edit temperature change for each location so it safely represents conditions anticipated.  Temperature change figures below are examples of maximum total swings from the lowest to the highest environmental temperatures at the indicated types of locations, and must be edited to represent temperature swings or changes that may occur at Project locations.

a. Outdoor Locations Not Exposed to Direct Sunlight:  [125 deg F (70 deg C)] <Insert temperature> temperature change.

b. Outdoor Locations Exposed to Direct Sunlight:  [155 deg F (86 deg C)] <Insert temperature> temperature change.

c. Indoor Spaces:  Connected with the Outdoors without Physical Separation:  [125 deg F (70 deg C)] <Insert temperature> temperature change.

d. Attics:  [135 deg F (75 deg C)] <Insert temperature> temperature change.

e. <Insert location and corresponding temperature change.>

Formula in first subparagraph below provides about 15 percent safety factor (extra expansion-contraction capability).

2. Install fitting(s) that provide expansion and contraction for at least 0.00041 inch per foot of length of straight run per deg F (0.06 mm per meter of length of straight run per deg C) of temperature change.

3. Install each expansion-joint fitting with position, mounting, and piston setting selected according to manufacturer's written instructions for conditions at specific location at the time of installation.

Delete option in first paragraph below if Type AC or MC cable is specified in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables" for lighting fixture connection.

O. Flexible Conduit Connections:  Use maximum of 72 inches (1830 mm) of flexible conduit for [recessed and semirecessed lighting fixtures, ]equipment subject to vibration, noise transmission, or movement; and for transformers and motors.

1. Use LFMC in damp or wet locations subject to severe physical damage.

2. Use LFMC or LFNC in damp or wet locations not subject to severe physical damage.

P. Recessed Boxes in Masonry Walls:  Saw-cut opening for box in center of cell of masonry block, and install box flush with surface of wall.

Q. Set metal floor boxes level and flush with finished floor surface.

R. Set nonmetallic floor boxes level.  Trim after installation to fit flush with finished floor surface.

3.3 INSTALLATION OF UNDERGROUND CONDUIT

Retain this Article if Project includes small amounts of exterior underground wiring, 600 V and less.  Delete if Division 26 Section "Underground Ducts and Raceways for Electrical Systems" is included in the Project Manual.  See Editing Instruction No. 3 in the Evaluations.

A. Direct-Buried Conduit:

1. Excavate trench bottom to provide firm and uniform support for conduit.  Prepare trench bottom as specified in Division 31 Section "Earth Moving" for pipe less than 6 inches (150 mm) in nominal diameter.

2. Install backfill as specified in Division 31 Section "Earth Moving."

3. After installing conduit, backfill and compact.  Start at tie-in point, and work toward end of conduit run, leaving conduit at end of run free to move with expansion and contraction as temperature changes during this process.  Firmly hand tamp backfill around conduit to provide maximum supporting strength.  After placing controlled backfill to within 12 inches (300 mm) of finished grade, make final conduit connection at end of run and complete backfilling with normal compaction as specified in Division 31 Section "Earth Moving."

Retain one of two subparagraphs below to specify type of stub-ups for direct-buried conduits in Project.

4. Install manufactured duct elbows for stub-ups at poles and equipment and at building entrances through the floor, unless otherwise indicated.  Encase elbows for stub-up ducts throughout the length of the elbow.

5. Install manufactured rigid steel conduit elbows for stub-ups at poles and equipment and at building entrances through the floor.

Retain first two subparagraphs below with either subparagraph above.

a. Couple steel conduits to ducts with adapters designed for this purpose, and encase coupling with 3 inches (75 mm) of concrete.

b. For stub-ups at equipment mounted on outdoor concrete bases, extend steel conduit horizontally a minimum of 60 inches (1500 mm) from edge of equipment pad or foundation.  Install insulated grounding bushings on terminations at equipment.

6. Warning Planks:  Bury warning planks approximately 12 inches (300 mm) above direct-buried conduits, placing them 24 inches (600 mm) o.c.  Align planks along the width and along the centerline of conduit.

3.4 INSTALLATION OF UNDERGROUND HANDHOLES AND BOXES

A. Install handholes and boxes level and plumb and with orientation and depth coordinated with connecting conduits to minimize bends and deflections required for proper entrances.

B. Unless otherwise indicated, support units on a level bed of crushed stone or gravel, graded from 1/2-inch (12.5-mm) sieve to No. 4 (4.75-mm) sieve and compacted to same density as adjacent undisturbed earth.

C. Elevation:  In paved areas, set so cover surface will be flush with finished grade.  Set covers of other enclosures 1 inch (25 mm) above finished grade.

D. Install handholes and boxes with bottom below the frost line, <Insert depth of frost line below grade at Project site> below grade.

Paragraph below requires Contractor to select hardware to install and support cable.  Delete if cable support is not required.  If desired, edit paragraph to refer Contractor to Drawings, and show specific requirements on Drawings for each enclosure.

E. Install removable hardware, including pulling eyes, cable stanchions, cable arms, and insulators, as required for installation and support of cables and conductors and as indicated.  Select arm lengths to be long enough to provide spare space for future cables, but short enough to preserve adequate working clearances in the enclosure.

Delete paragraph below if conduits enter enclosure through open bottom.

F. Field-cut openings for conduits according to enclosure manufacturer's written instructions.  Cut wall of enclosure with a tool designed for material to be cut.  Size holes for terminating fittings to be used, and seal around penetrations after fittings are installed.

3.5 SLEEVE INSTALLATION FOR ELECTRICAL PENETRATIONS

A. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 07 Section "Penetration Firestopping."

B. Concrete Slabs and Walls:  Install sleeves for penetrations unless core-drilled holes or formed openings are used.  Install sleeves during erection of slabs and walls.

C. Use pipe sleeves unless penetration arrangement requires rectangular sleeved opening.

D. Rectangular Sleeve Minimum Metal Thickness:

1. For sleeve cross-section rectangle perimeter less than 50 inches (1270 mm) and no side greater than 16 inches (400 mm), thickness shall be 0.052 inch (1.3 mm).

2. For sleeve cross-section rectangle perimeter equal to, or greater than, 50 inches (1270 mm) and 1 or more sides equal to, or greater than, 16 inches (400 mm), thickness shall be 0.138 inch (3.5 mm).

E. Fire-Rated Assemblies:  Install sleeves for penetrations of fire-rated floor and wall assemblies unless openings compatible with firestop system used are fabricated during construction of floor or wall.

Edit first paragraph below as required for 2-inch (50-mm) extension above floor.

F. Cut sleeves to length for mounting flush with both surfaces of walls.

G. Extend sleeves installed in floors 2 inches (50 mm) above finished floor level.

Edit paragraph below as required for Project design conditions and seismic-criteria status.

H. Size pipe sleeves to provide 1/4-inch (6.4-mm) annular clear space between sleeve and raceway unless sleeve seal is to be installed[ or unless seismic criteria require different clearance].

Retain first paragraph below if external sealing is required.

I. Seal space outside of sleeves with grout for penetrations of concrete and masonry[ and with approved joint compound for gypsum board assemblies].

J. Interior Penetrations of Non-Fire-Rated Walls and Floors:  Seal annular space between sleeve and raceway, using joint sealant appropriate for size, depth, and location of joint.  Refer to Division 07 Section "Joint Sealants" for materials and installation.

K. Fire-Rated-Assembly Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at raceway penetrations.  Install sleeves and seal with firestop materials.  Comply with Division 07 Section "Penetration Firestopping."

L. Roof-Penetration Sleeves:  Seal penetration of individual raceways with flexible, boot-type flashing units applied in coordination with roofing work.

M. Aboveground, Exterior-Wall Penetrations:  Seal penetrations using sleeves and mechanical sleeve seals.  Select sleeve size to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

N. Underground, Exterior-Wall Penetrations:  Install cast-iron "wall pipes" for sleeves.  Size sleeves to allow for 1-inch (25-mm) annular clear space between raceway and sleeve for installing mechanical sleeve seals.

3.6 SLEEVE-SEAL INSTALLATION

A. Install to seal underground, exterior wall penetrations.

B. Use type and number of sealing elements recommended by manufacturer for raceway material and size.  Position raceway in center of sleeve.  Assemble mechanical sleeve seals and install in annular space between raceway and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

3.7 FIRESTOPPING

A. Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly.  Firestopping materials and installation requirements are specified in Division 07 Section "Penetration Firestopping."

3.8 PROTECTION

A. Provide final protection and maintain conditions that ensure coatings, finishes, and cabinets are without damage or deterioration at time of Substantial Completion.

1. Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

2. Repair damage to PVC or paint finishes with matching touchup coating recommended by manufacturer.

END OF SECTION 260533

	RACEWAY AND BOXES FOR ELECTRICAL SYSTEMS
	260533 - 1



