Copyright 2005 AIA
MASTERSPEC Full Length
03/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 271500 - COMMUNICATIONS HORIZONTAL CABLING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Pathways.

2. UTP cabling.

3. [50/125] [62.5/125]-micrometer, optical fiber cabling.

4. Coaxial cable.

5. Multiuser telecommunications outlet assemblies.

6. Cable connecting hardware, patch panels, and cross-connects.

7. Telecommunications outlet/connectors.

8. Cabling system identification products.

9. Cable management system.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 27 Section "Communications Backbone Cabling" for voice and data cabling associated with system panels and devices.

2. Division 28 Section "Conductors and Cables for Electronic Safety and Security" for voice and data cabling associated with system panels and devices.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. Basket Cable Tray:  A fabricated structure consisting of wire mesh bottom and side rails.

B. BICSI:  Building Industry Consulting Service International.

C. Channel Cable Tray:  A fabricated structure consisting of a one-piece, ventilated-bottom or solid-bottom channel.

D. Consolidation Point:  A location for interconnection between horizontal cables extending from building pathways and horizontal cables extending into furniture pathways.

E. Cross-Connect:  A facility enabling the termination of cable elements and their interconnection or cross-connection.

F. EMI:  Electromagnetic interference.

G. IDC:  Insulation displacement connector.

H. Ladder Cable Tray:  A fabricated structure consisting of two longitudinal side rails connected by individual transverse members (rungs).

I. LAN:  Local area network.

J. MUTOA:  Multiuser telecommunications outlet assembly, a grouping in one location of several telecommunications outlet/connectors.

K. Outlet/Connectors:  A connecting device in the work area on which horizontal cable or outlet cable terminates.

L. RCDD:  Registered Communications Distribution Designer.

M. Solid-Bottom or Nonventilated Cable Tray:  A fabricated structure consisting of longitudinal side rails and a bottom without ventilation openings.

N. Trough or Ventilated Cable Tray:  A fabricated structure consisting of longitudinal side rails and a bottom having openings for the passage of air.

O. UTP:  Unshielded twisted pair.

1.4 HORIZONTAL CABLING DESCRIPTION

A. Horizontal cable and its connecting hardware provide the means of transporting signals between the telecommunications outlet/connector and the horizontal cross-connect located in the communications equipment room.  This cabling and its connecting hardware are called "permanent link," a term that is used in the testing protocols.

1. TIA/EIA-568-B.1 requires that a minimum of two telecommunications outlet/connectors be installed for each work area.

2. Horizontal cabling shall contain no more that one transition point or consolidation point between the horizontal cross-connect and the telecommunications outlet/connector.

3. Bridged taps and splices shall not be installed in the horizontal cabling.

4. Splitters shall not be installed as part of the optical fiber cabling.

B. A work area is approximately 100 sq. ft. (9.3 sq. m), and includes the components that extend from the telecommunications outlet/connectors to the station equipment.

C. The maximum allowable horizontal cable length is 295 feet (90 m).  This maximum allowable length does not include an allowance for the length of 16 feet (4.9 m) to the workstation equipment.  The maximum allowable length does not include an allowance for the length of 16 feet (4.9 m) in the horizontal cross-connect.

1.5 PERFORMANCE REQUIREMENTS

A. General Performance:  Horizontal cabling system shall comply with transmission standards in TIA/EIA-568-B.1, when tested according to test procedures of this standard.

1.6 SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.

Retain subparagraph below for coaxial cable.  Installation data for UTP and optical fiber cabling are specified in the referenced TIA/EIA standards.

1. For coaxial cable, include the following installation data for each type used:

a. Nominal OD.

b. Minimum bending radius.

c. Maximum pulling tension.

B. Shop Drawings:

Retain one of first two subparagraphs below.

1. System Labeling Schedules:  Electronic copy of labeling schedules, in software and format selected by Owner.

2. System Labeling Schedules:  Electronic copy of labeling schedules that are part of the cabling and asset identification system of the software.

3. Cabling administration drawings and printouts.

4. Wiring diagrams to show typical wiring schematics, including the following:

a. Cross-connects.

b. Patch panels.

c. Patch cords.

5. Cross-connects and patch panels.  Detail mounting assemblies, and show elevations and physical relationship between the installed components.

6. Cable tray layout, showing cable tray route to scale, with relationship between the tray and adjacent structural, electrical, and mechanical elements.  Include the following:

a. Vertical and horizontal offsets and transitions.

b. Clearances for access above and to side of cable trays.

c. Vertical elevation of cable trays above the floor or bottom of ceiling structure.

d. Load calculations to show dead and live loads as not exceeding manufacturer's rating for tray and its support elements.

Retain first paragraph below when workstation outlet faceplates have critical features needing hands-on appraisal.

C. Samples:  For workstation outlets, jacks, jack assemblies, [in specified finish, one for each size and outlet configuration] [and faceplates for color selection and evaluation of technical features].

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For [Installer, ]qualified layout technician, installation supervisor, and field inspector.

E. Source quality-control reports.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

F. Field quality-control reports.

G. Maintenance Data:  For splices and connectors to include in maintenance manuals.

Retain paragraph below for PC-based cabling administration systems.

H. Software and Firmware Operational Documentation:

1. Software operating and upgrade manuals.

2. Program Software Backup:  On magnetic media or compact disk, complete with data files.

3. Device address list.

4. Printout of software application and graphic screens.

1.7 QUALITY ASSURANCE

BICSI is an industry trade association.  See Editing Instruction No. 2 in the Evaluations for summaries of qualifications for registration.

A. Installer Qualifications:  Cabling Installer must have personnel certified by BICSI on staff.

1. Layout Responsibility:  Preparation of Shop Drawings[ and Cabling Administration Drawings][, Cabling Administration Drawings, and field testing program development] by an RCDD.

2. Installation Supervision:  Installation shall be under the direct supervision of [Registered Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

Delete subparagraph below if Contractor performs field quality control.

3. Testing Supervisor:  Currently certified by BICSI as an RCDD to supervise on-site testing.

Retain first paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 01 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

B. Testing Agency Qualifications:  An NRTL.

1. Testing Agency's Field Supervisor:  Currently certified by BICSI as an RCDD to supervise on-site testing.

C. Surface-Burning Characteristics:  As determined by testing identical products according to ASTM E 84 by a qualified testing agency.  Identify products with appropriate markings of applicable testing agency.

1. Flame-Spread Index:  [25] <Insert value> or less.

2. Smoke-Developed Index:  [50] [450] <Insert value> or less.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

E. Telecommunications Pathways and Spaces:  Comply with TIA/EIA-569-A.

F. Grounding:  Comply with ANSI-J-STD-607-A.

1.8 DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIM, cables should be tested upon receipt.

A. Test cables upon receipt at Project site.

Retain one or both of first two subparagraphs below.

1. Test optical fiber cables to determine the continuity of the strand end to end.  Use [optical fiber flashlight] [or] [optical loss test set] <Insert test>.

2. Test optical fiber cables while on reels.  Use an optical time domain reflectometer to verify the cable length and locate cable defects, splices, and connector; including the loss value of each.  Retain test data and include the record in maintenance data.

3. Test each pair of UTP cable for open and short circuits.

1.9 PROJECT CONDITIONS

A. Environmental Limitations:  Do not deliver or install cables and connecting materials until wet work in spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

1.10 COORDINATION

Revise this article to specify coordination with other parties involved in finalizing communications equipment room work.  See Editing Instruction No. 3 in the Evaluations.

A. Coordinate layout and installation of telecommunications pathways and cabling with Owner's telecommunications and LAN equipment and service suppliers.

B. Coordinate telecommunications outlet/connector locations with location of power receptacles at each work area.

1.11 SOFTWARE SERVICE AGREEMENT

Services in this article may not be allowed for publicly funded projects.

Retain this article for computer-based, special-purpose cabling administration software.

A. Technical Support:  Beginning with Substantial Completion, provide software support for [two] <Insert number> years.

B. Upgrade Service:  Update software to latest version at Project completion.  Install and program software upgrades that become available within [two] <Insert number> years from date of Substantial Completion.  Upgrading software shall include operating system.  Upgrade shall include new or revised licenses for use of software.

1. Provide [30] <Insert number> days' notice to Owner to allow scheduling and access to system and to allow Owner to upgrade computer equipment if necessary.

1.12 EXTRA MATERIALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Patch-Panel Units:  [One] <Insert number> of each type.

2. Connecting Blocks:  [One] <Insert number> of each type.

3. Device Plates:  [One] <Insert number> of each type.

4. Multiuser Telecommunications Outlet Assemblies:  [One] <Insert number> of each type.

PART 2 -  PRODUCTS

2.1 PATHWAYS

A. General Requirements:  Comply with TIA/EIA-569-A.

Retain first paragraph below if cable support brackets are used in communications equipment room.

B. Cable Support:  NRTL labeled for support of Category 6 cabling, designed to prevent degradation of cable performance and pinch points that could damage cable.

1. Support brackets with cable tie slots for fastening cable ties to brackets.

2. Lacing bars, spools, J-hooks, and D-rings.

3. Straps and other devices.

C. Cable Trays:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cable Management Solutions, Inc.

b. Cablofil Inc.

c. Cooper B-Line, Inc.

d. Cope - Tyco/Allied Tube & Conduit.

e. GS Metals Corp.

f. <Insert manufacturer's name>.

Besides two corrosion-protection options in subparagraph below, alternative methods include trays fabricated from Types 304 and 316 stainless steel, steel with electrogalvanized zinc plating and coated with yellow dichromate, steel coated with PVC, and steel with powder coating.

2. Cable Tray Materials:  Metal, suitable for indoors, and protected against corrosion by [electroplated zinc galvanizing, complying with ASTM B 633, Type 1, not less than 0.000472 inch (0.012 mm) thick] [hot-dip galvanizing, complying with ASTM A 123/A 123M, Grade 0.55, not less than 0.002165 inch (0.055 mm) thick].

Retain one or more of five subparagraphs below.  If multiple types or various dimensions are required, delete five subparagraphs and indicate location and dimensions on Drawings.  Trays in first subparagraph are generally available in widths of between 2 and 24 inches (50 and 600 mm) and in depths of between 1 and 4 inches (25 and 100 mm).

a. Basket Cable Trays:  [6 inches (150 mm) wide and 2 inches (50 mm) deep] <Insert dimensions>.  Wire mesh spacing shall not exceed 2 by 4 inches (50 by 100 mm).

Trays in first subparagraph below are generally available in widths of between 6 and 36 inches (150 and 915 mm).

b. Trough Cable Trays:  [Nominally 6 inches (150 mm)] <Insert dimension> wide.

Trays in first subparagraph below are generally available in widths of between 6 and 36 inches (150 and 915 mm) and in rung spacings of between 6 and 18 inches (150 and 455 mm).

c. Ladder Cable Trays:  [Nominally 18 inches (455 mm)] <Insert dimension> wide, and a rung spacing of [12 inches (305 mm)] <Insert spacing>.

Trays in first subparagraph below are generally available in widths of 3, 4, and 6 inches (75, 100, and 150 mm).

d. Channel Cable Trays:  One-piece construction, [nominally 4 inches (100 mm)] <Insert dimension> wide.  Slot spacing shall not exceed 4-1/2 inches (115 mm) o.c.

Trays in subparagraph below are generally available in widths of between 6 and 36 inches (150 and 915 mm).

e. Solid-Bottom Cable Trays:  One-piece construction, [nominally 12 inches (305 mm)] <Insert dimension> wide.  Provide [with] [without] solid covers.

D. Conduit and Boxes:  Comply with requirements in Division 26 Section "Raceway and Boxes for Electrical Systems."[  Flexible metal conduit shall not be used.]

1. Outlet boxes shall be no smaller than 2 inches (50 mm) wide, 3 inches (75 mm) high, and 2-1/2 inches (64 mm) deep.

2.2 BACKBOARDS

A. Backboards:  Plywood, [fire-retardant treated,]3/4 by 48 by 96 inches (19 by 1220 by 2440 mm).  Comply with requirements in Division 06 Section "Rough Carpentry" for plywood backing panels.

2.3 UTP CABLE

Copy this article and re-edit for each product.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Belden CDT Inc.; Electronics Division.

2. Berk-Tek; a Nexans company.

3. CommScope, Inc.

4. Draka USA.

5. Genesis Cable Products; Honeywell International, Inc.

6. KRONE Incorporated.

7. Mohawk; a division of Belden CDT.

8. Nordex/CDT; a subsidiary of Cable Design Technologies.

9. Superior Essex Inc.

10. SYSTIMAX Solutions; a CommScope, Inc. brand.

11. 3M.

12. Tyco Electronics/AMP Netconnect; Tyco International Ltd.

13. <Insert manufacturer's name>.

B. Description:  100-ohm, 4-pair UTP, formed into 25-pair, binder groups covered with a blue thermoplastic jacket.

1. Comply with ICEA S-90-661 for mechanical properties.

2. Comply with TIA/EIA-568-B.1 for performance specifications.

3. Comply with TIA/EIA-568-B.2, [Category 5e] [Category 6].

4. Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

a. Communications, General Purpose:  Type CM or CMG[; or MPP, CMP, MPR, CMR, MP, or MPG].

b. Communications, Plenum Rated:  Type CMP[ or MPP], complying with NFPA 262.

c. Communications, Riser Rated:  Type CMR[; or MPP, CMP, or MPR], complying with UL 1666.

d. Communications, Limited Purpose:  Type CMX[; or MPP, CMP, MPR, CMR, MP, MPG, CM, or CMG].

e. Multipurpose:  Type MP or MPG[; or MPP or MPR].

f. Multipurpose, Plenum Rated:  Type MPP, complying with NFPA 262.

g. Multipurpose, Riser Rated:  Type MPR[ or MPP], complying with UL 1666.

2.4 UTP CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. American Technology Systems Industries, Inc.

2. Dynacom Corporation.

3. Hubbell Premise Wiring.

4. KRONE Incorporated.

5. Leviton Voice & Data Division.

6. Molex Premise Networks; a division of Molex, Inc.

7. Nordex/CDT; a subsidiary of Cable Design Technologies.

8. Panduit Corp.

9. Siemon Co. (The).

10. Tyco Electronics/AMP Netconnect; Tyco International Ltd.

11. <Insert manufacturer's name>.

See Editing Instruction No. 4 in the Evaluations for discussion about 110-style IDC connectors and connector blocks.

B. General Requirements for Cable Connecting Hardware:  Comply with TIA/EIA-568-B.2, IDC type, with modules designed for punch-down caps or tools.  Cables shall be terminated with connecting hardware of same category or higher.

C. Connecting Blocks:  [110-style IDC for Category 5e] [110-style IDC for Category 6] [66-style IDC for Category 5e].  Provide blocks for the number of cables terminated on the block, plus [25] <Insert number> percent spare.  Integral with connector bodies, including plugs and jacks where indicated.

Delete first paragraph below if cross-connection is accomplished exclusively on patch panels.

D. Cross-Connect:  Modular array of connecting blocks arranged to terminate building cables and permit interconnection between cables.

Coordinate subparagraph below with Drawings for quantity of terminals.

1. Number of Terminals per Field:  [One] <Insert number> for each conductor in assigned cables.

E. Patch Panel:  Modular panels housing multiple-numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Coordinate subparagraph below with Drawings for quantity of fields.

1. Number of Jacks per Field:  [One] <Insert number> for each four-pair [UTP cable indicated] [conductor group of indicated cables, plus spares and blank positions adequate to suit specified expansion criteria].

F. Jacks and Jack Assemblies:  Modular, color-coded, eight-position modular receptacle units with integral IDC-type terminals.

Cords are generally available in lengths to 20 feet (6 m) and longer in 24-inch (600-mm) increments.

G. Patch Cords:  Factory-made, four-pair cables in [36-inch (900 mm)] [48-inch (1200-mm)] <Insert length> lengths; terminated with eight-position modular plug at each end.

Retain one of two subparagraphs below; retain first for Category 6, second for Category 5e patch cords.

1. Patch cords shall have bend-relief-compliant boots and color-coded icons to ensure Category 6 performance.  Patch cords shall have latch guards to protect against snagging.

2. Patch cords shall have color-coded boots for circuit identification.

2.5 OPTICAL FIBER CABLE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Berk-Tek; a Nexans company.

2. CommScope, Inc.

3. Corning Cable Systems.

4. General Cable Technologies Corporation.

5. Mohawk; a division of Belden CDT.

6. Nordex/CDT; a subsidiary of Cable Design Technologies.

7. Optical Connectivity Solutions Division; Emerson Network Power.

8. Superior Essex Inc.

9. SYSTIMAX Solutions; a CommScope, Inc. brand.

10. 3M.

11. Tyco Electronics/AMP Netconnect; Tyco International Ltd.

12. <Insert manufacturer's name>.

B. Description:  Multimode, [50/125] [62.5/125]-micrometer, [24] <Insert number>-fiber, [nonconductive, ]tight buffer, optical fiber cable.

Retain first subparagraph below for indoor cable.  ICEA standard for outside plant is ICEA S-87-640.

1. Comply with ICEA S-83-596 for mechanical properties.

2. Comply with TIA/EIA-568-B.3 for performance specifications.

Retain first option in first subparagraph below for 50/125-micrometer cable; retain second for 62.5/125-micrometer cable.

3. Comply with [TIA/EIA-492AAAA-B] [TIA/EIA-492AAAA-A] for detailed specifications.

4. Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444, UL 1651, and NFPA 70 for the following types:

Type requirements in first six subparagraphs below are minimum requirements and may need to be revised to suit Project.  OFC, OFCR, OFCG, and OFCP are conductive optical fiber cables that might have application in industrial settings.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

a. General Purpose, Nonconductive:  Type OFN or OFNG[, or OFNR, OFNP].

b. Plenum Rated, Nonconductive:  Type OFNP, complying with NFPA 262.

c. Riser Rated, Nonconductive:  Type OFNR[ or OFNP], complying with UL 1666.

d. General Purpose, Conductive:  Type OFC or OFCG[; or OFNG, OFN, OFCR, OFNR, OFCP, or OFNP].

e. Plenum Rated, Conductive:  Type OFCP[ or OFNP], complying with NFPA 262.

f. Riser Rated, Conductive:  Type OFCR[; or OFNR, OFCP, or OFNP], complying with UL 1666.

Retain first subparagraph below even if nonconductive cable is specified in subparagraphs above.  If both conductive and nonconductive cables are specified, indicate locations of each on Drawings.

5. Conductive cable shall be [steel] [aluminum] armored type.

6. Maximum Attenuation:  [3.50] <Insert number> dB/km at 850 nm; [1.5] <Insert number> dB/km at 1300 nm.

7. Minimum Modal Bandwidth:  160 MHz-km at 850 nm; 500 MHz-km at 1300 nm.

C. Jacket:

1. Jacket Color:  [Aqua for 50/125-micrometer cable] [Orange for 62.5/125-micrometer cable] .

2. Cable cordage jacket, fiber, unit, and group color shall be according to TIA/EIA-598-B.

3. Imprinted with fiber count, fiber type, and aggregate length at regular intervals not to exceed 40 inches (1000 mm).

2.6 OPTICAL FIBER CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. ADC.

2. American Technology Systems Industries, Inc.

3. Berk-Tek; a Nexans company.

4. Corning Cable Systems.

5. Dynacom Corporation.

6. Hubbell Premise Wiring.

7. Molex Premise Networks; a division of Molex, Inc.

8. Nordex/CDT; a subsidiary of Cable Design Technologies.

9. Optical Connectivity Solutions Division; Emerson Network Power.

10. Siemon Co. (The).

11. <Insert manufacturer's name>.

B. Cross-Connects and Patch Panels:  Modular panels housing multiple-numbered, duplex cable connectors.

Coordinate subparagraph below with Drawings for quantity of connectors.

1. Number of Connectors per Field:  [One] <Insert number> for each fiber of cable or cables assigned to field, plus spares and blank positions adequate to suit specified expansion criteria.

C. Patch Cords:  Factory-made, dual-fiber cables in 36-inch (900-mm) lengths.

D. Cable Connecting Hardware:

1. Comply with Optical Fiber Connector Intermateability Standards (FOCIS) specifications of TIA/EIA-604-2, TIA/EIA-604-3-A, and TIA/EIA-604-12.  Comply with TIA/EIA-568-B.3.

Type SC is a subscriber connector, Type ST is a straight-tip, single-fiber connector; both are in common use.  Recently developed connectors are Type LC, which is an upgraded version of either Type SC or ST connector with a lower insertion loss, and Type MT-RJ, which is a no-epoxy, no-polish connector.

2. Quick-connect, simplex and duplex, [Type SC] [Type ST] [Type LC] [Type MT-RJ] connectors.  Insertion loss not more than 0.75 dB.

3. Type SFF connectors may be used in termination racks, panels, and equipment packages.

2.7 COAXIAL CABLE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Alpha Wire Company.

2. Belden CDT Inc.; Electronics Division.

3. Coleman Cable, Inc.

4. CommScope, Inc.

5. Draka USA.

6. <Insert manufacturer's name>.

See Evaluations for discussion about coaxial cables.  Indicate location of each type on Drawings.

B. Cable Characteristics:  Broadband type, recommended by cable manufacturer specifically for broadband data transmission applications.  Coaxial cable and accessories shall have 75-ohm nominal impedance with a return loss of 20 dB maximum from 7 to 806 MHz.

Cable types in first five paragraphs below are typical.

C. RG-11/U:  NFPA 70, Type CATV.

1. No. [14] <Insert size> AWG, solid, copper-covered steel conductor.

2. Gas-injected, foam-PE insulation.

3. Double shielded with 100 percent aluminum polyester tape and 60 percent aluminum braid.

4. Jacketed with sunlight-resistant, black PVC or PE.

5. Suitable for outdoor installations in ambient temperatures ranging from minus 40 to plus 85 deg C.

D. RG59/U:  NFPA 70, Type CATVR.

1. No. [20] <Insert size> AWG, solid, silver-plated, copper-covered steel conductor.

2. Gas-injected, foam-PE insulation.

3. Triple shielded with 100 percent aluminum polyester tape and 95 percent aluminum braid; covered by aluminum foil with grounding strip.

4. Color-coded PVC jacket.

E. RG-6/U:  NFPA 70, Type CATV or CM.

1. No. [16] <Insert size> AWG, solid, copper-covered steel conductor; gas-injected, foam-PE insulation.

2. Double shielded with 100 percent aluminum-foil shield and 60 percent aluminum braid.

3. Jacketed with black PVC or PE.

4. Suitable for indoor installations.

F. RG59/U:  NFPA 70, Type CATV.

1. No. [20] <Insert size> AWG, solid, copper-covered steel conductor; gas-injected, foam-PE insulation.

2. Double shielded with 100 percent aluminum polyester tape and 40 percent aluminum braid.

3. PVC jacket.

G. RG59/U (Plenum Rated):  NFPA 70, Type CMP.

1. No. [20] <Insert size> AWG, solid, copper-covered steel conductor; foam fluorinated ethylene propylene insulation.

2. Double shielded with 100 percent aluminum-foil shield and 65 percent aluminum braid.

3. Copolymer jacket.

Paragraph below is typical of NFPA 70 cable types.  See NFPA 70, "Community Antenna Television and Radio Distribution Systems" and "Network-Powered Broadband Communications Systems" Articles for other types that may be added to the list.

H. NFPA and UL compliance, listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 1655 and with NFPA 70 "Radio and Television Equipment" and "Community Antenna Television and Radio Distribution" Articles.  Types are as follows:

1. CATV Cable:  Type CATV[, or CATVP or CATVR].

2. CATV Plenum Rated:  Type CATVP, complying with NFPA 262.

3. CATV Riser Rated:  Type CATVR[; or CATVP, CATVR, or CATV], complying with UL 1666.

4. CATV Limited Rating:  Type CATVX.

2.8 COAXIAL CABLE HARDWARE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Aim Electronics; a brand of Emerson Electric Co.

2. Leviton Voice & Data Division.

3. Siemon Co. (The).

4. <Insert manufacturer's name>.

B. Coaxial-Cable Connectors:  Type BNC, 75 ohms.

2.9 CONSOLIDATION POINTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. American Technology Systems Industries, Inc.

2. Chatsworth Products, Inc.

3. Dynacom Corporation.

4. Hubbell Premise Wiring.

5. Molex Premise Networks; a division of Molex, Inc.

6. Nordex/CDT; a subsidiary of Cable Design Technologies.

7. Ortronics, Inc.

8. Panduit Corp.

9. Siemon Co. (The).

10. <Insert manufacturer's name>.

B. Description:  Consolidation points shall comply with requirements for cable connecting hardware.

Coordinate first subparagraph below with Drawings for quantity of terminals.

1. Number of Terminals per Field:  [One] <Insert number> for each conductor in assigned cables.

Coordinate first subparagraph below with Drawings for quantity of connectors.

2. Number of Connectors per Field:

a. [One] <Insert number> for each four-pair UTP cable indicated.

b. [One] <Insert number> for each four-pair conductor group of indicated cables, plus [25] <Insert number> percent spare positions.

3. Mounting:  [Recessed in ceiling] [Wall] [Desk] [Furniture].

4. NRTL listed as complying with UL 50 and UL 1863.

5. When installed in plenums used for environmental air, NRTL listed as complying with UL 2043.

2.10 MULTIUSER TELECOMMUNICATIONS OUTLET ASSEMBLY (MUTOA)

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Chatsworth Products, Inc.

2. Hubbell Premise Wiring.

3. Molex Premise Networks; a division of Molex, Inc.

4. Nordex/CDT; a subsidiary of Cable Design Technologies.

5. Ortronics, Inc.

6. Panduit Corp.

7. Siemon Co. (The).

8. <Insert manufacturer's name>.

B. Description:  MUTOAs shall meet the requirements for cable connecting hardware.

Coordinate first subparagraph below with Drawings for quantity of terminals.

1. Number of Terminals per Field:  [One] <Insert number> for each conductor in assigned cables.

Coordinate first subparagraph below with Drawings for quantity of connectors.

2. Number of Connectors per Field:

a. [One] <Insert number> for each four-pair UTP cable indicated.

b. [One] <Insert number> for each four-pair conductor group of indicated cables, plus [25] <Insert number> percent spare positions.

3. Mounting:  [Recessed in ceiling] [Wall] [Desk] [Furniture].

4. NRTL listed as complying with UL 50 and UL 1863.

5. Label shall include maximum length of work area cords, based on TIA/EIA-568-B.1.

6. When installed in plenums used for environmental air, NRTL listed as complying with UL 2043.

2.11 TELECOMMUNICATIONS OUTLET/CONNECTORS

A. Jacks:  100-ohm, balanced, twisted-pair connector; four-pair, eight-position modular.  Comply with TIA/EIA-568-B.1.

Coordinate paragraph below with other items specified to be mounted in workstation faceplates.  Revise paragraph if faceplate elevations are on Drawings.

B. Workstation Outlets:  [Two] [Four] <Insert number of ports>-port-connector assemblies mounted in [single] [or] [multigang] faceplate.

Retain one of first two subparagraphs below, or retain both as required to match Division 26 Section "Wiring Devices."

1. Plastic Faceplate:  High-impact plastic.  Coordinate color with Division 26 Section "Wiring Devices."

2. Metal Faceplate:  [Stainless steel] [Brass] <Insert description>, complying with requirements in Division 26 Section "Wiring Devices."

3. For use with snap-in jacks accommodating any combination of UTP, optical fiber, and coaxial work area cords.

a. Flush mounting jacks, positioning the cord at a 45-degree angle.

Retain one of three subparagraphs below; retain first for metal faceplates.

4. Legend:  Factory labeled by silk-screening or engraving [for] [stainless steel] [brass] <Insert description> [faceplates].

5. Legend:  Machine printed, in the field, using adhesive-tape label.

6. Legend:  Snap-in, clear-label covers and machine-printed paper inserts.

2.12 GROUNDING

A. Comply with requirements in Division 26 Section "Grounding and Bonding for Electrical Systems" for grounding conductors and connectors.

B. Comply with ANSI-J-STD-607-A.

2.13 IDENTIFICATION PRODUCTS

A. Comply with TIA/EIA-606-A and UL 969 for labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

B. Comply with requirements in Division 26 Section "Identification for Electrical Systems."

2.14 CABLE MANAGEMENT SYSTEM

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. iTRACS Corporation.

2. Telsoft Solutions.

3. <Insert manufacturer's name>.

C. Description:  Computer-based cable management system, with integrated database[ and graphic] capabilities.

First paragraph below specifies identification that is integrated with database functions, testing, and graphics.

D. Document physical characteristics by recording the network, TIA/EIA details, and connections between equipment and cable.

E. Information shall be presented in database view[, schematic plans, or technical drawings].

Retain subparagraph below if graphic capability is included.

1. [Microsoft Visio Professional] [or] [AutoCAD] drawing software shall be used as drawing and schematic plans software.

Retain paragraph below to combine cable testing with printing of labels.

F. System shall interface with the following testing and recording devices:

1. Direct upload tests from circuit testing instrument into the personal computer.

2. Direct download circuit labeling into labeling printer.

2.15 SOURCE QUALITY CONTROL

Retain first paragraph below if required.  Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

A. Testing Agency:  Engage a qualified testing agency to evaluate cables.

B. Factory test UTP and optical fiber cables on reels according to TIA/EIA-568-B.1.

C. Factory test UTP cables according to TIA/EIA-568-B.2.

D. Factory test multimode optical fiber cables according to TIA/EIA-526-14-A and TIA/EIA-568-B.3.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

E. Factory-sweep test coaxial cables at frequencies from 5 MHz to 1 GHz.  Sweep test shall test the frequency response, or attenuation over frequency, of a cable by generating a voltage whose frequency is varied through the specified frequency range and graphing the results.

F. Cable will be considered defective if it does not pass tests and inspections.

G. Prepare test and inspection reports.

PART 3 -  EXECUTION

3.1 ENTRANCE FACILITIES

Retain this article if service entrance cabling and demarcation point are provided by communications service provider and horizontal cabling connects to the demarcation point.  Normally, unless this is for a small single-story facility, communications horizontal cable interfaces with backbone cabling in communications rooms or spaces at cross-connects and patch panels

A. Coordinate backbone cabling with the protectors and demarcation point provided by communications service provider.

3.2 WIRING METHODS

Retain one of first two paragraphs below and coordinate with Drawings.  Delete both if wiring methods for system are indicated on Drawings.

A. Wiring Method:  Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters[ and except in accessible ceiling spaces, in attics, and in gypsum board partitions where unenclosed wiring method may be used].  Conceal raceway and cables except in unfinished spaces.

Retain first subparagraph below if retaining unenclosed wiring method option in paragraph above.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements for raceways and boxes specified in Division 26 Section "Raceway and Boxes for Electrical Systems."

B. Wiring Method:  Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

C. Wiring within Enclosures:  Bundle, lace, and train cables to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.  Provide and use lacing bars and distribution spools.

3.3 INSTALLATION OF PATHWAYS

A. Cable Trays:  Comply with NEMA VE 2 and TIA/EIA-569-A-7.

Coordinate cable connection hardware installations and specialty arrangements with layout drawings and with requirements specified for communications equipment rooms.  If Drawings are explicit enough, these requirements may be reduced or omitted.

B. Comply with requirements for demarcation point, pathways, cabinets, and racks specified in Division 27 Section "Communications Equipment Room Fittings."  Drawings indicate general arrangement of pathways and fittings.

C. Comply with TIA/EIA-569-A for pull-box sizing and length of conduit and number of bends between pull points.

D. Comply with requirements in Division 26 Section "Raceway and Boxes for Electrical Systems" for installation of conduits and wireways.

E. Install manufactured conduit sweeps and long-radius elbows whenever possible.

F. Pathway Installation in Communications Equipment Rooms:

1. Position conduit ends adjacent to a corner on backboard where a single piece of plywood is installed, or in the corner of room where multiple sheets of plywood are installed around perimeter walls of room.

2. Install cable trays to route cables if conduits cannot be located in these positions.

3. Secure conduits to backboard when entering room from overhead.

4. Extend conduits [3 inches (76 mm)] <Insert dimension> above finished floor.

5. Install metal conduits with grounding bushings and connect with grounding conductor to grounding system.

G. Backboards:  Install backboards with 96-inch (2440-mm) dimension vertical.  Butt adjacent sheets tightly, and form smooth gap-free corners and joints.

3.4 INSTALLATION OF CABLES

A. Comply with NECA 1.

B. General Requirements for Cabling:

1. Comply with TIA/EIA-568-B.1.

2. Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

3. Install 110-style IDC termination hardware unless otherwise indicated.

4. MUTOA shall not be used as a cross-connect point.

5. Consolidation points may be used only for making a direct connection to telecommunications outlet/connectors:

a. Do not use consolidation point as a cross-connect point, as a patch connection, or for direct connection to workstation equipment.

b. Locate consolidation points for UTP at least 49 feet (15 m) from communications equipment room.

6. Terminate conductors; no cable shall contain unterminated elements.  Make terminations only at indicated outlets, terminals, cross-connects, and patch panels.

7. Cables may not be spliced.  Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

8. Install lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

9. Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter.  Install lacing bars and distribution spools.

10. Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between termination, tap, or junction points.  Remove and discard cable if damaged during installation and replace it with new cable.

11. Cold-Weather Installation:  Bring cable to room temperature before dereeling.  Heat lamps shall not be used for heating.

12. In the communications equipment room, install a 10-foot- (3-m-) long service loop on each end of cable.

13. Pulling Cable:  Comply with BICSI ITSIM, Ch. 4, "Pulling Cable."  Monitor cable pull tensions.

C. UTP Cable Installation:

1. Comply with TIA/EIA-568-B.2.

2. Do not untwist UTP cables more than 1/2 inch (12 mm) from the point of termination to maintain cable geometry.

D. Optical Fiber Cable Installation:

1. Comply with TIA/EIA-568-B.3.

2. Cable may be terminated on connecting hardware that is rack or cabinet mounted.

E. Open-Cable Installation:

1. Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

2. Suspend UTP cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceilings by cable supports not more than [60 inches (1524 mm)] <Insert dimension> apart.

3. Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

F. Installation of Cable Routed Exposed under Raised Floors:

1. Install plenum-rated cable only.

2. Install cabling after the flooring system has been installed in raised floor areas.

3. Coil cable [6 feet (1800 mm)] <Insert size> long not less than [12 inches (300 mm)] <Insert size> in diameter below each feed point.

G. Outdoor Coaxial Cable Installation:

1. Install outdoor connections in enclosures complying with NEMA 250, Type 4X.  Install corrosion-resistant connectors with properly designed O-rings to keep out moisture.

2. Attach antenna lead-in cable to support structure at intervals not exceeding 36 inches (915 mm).

H. Group connecting hardware for cables into separate logical fields.

See Editing Instruction No. 5 in the Evaluations for discussion about EMI.

I. Separation from EMI Sources:

1. Comply with BICSI TDMM and TIA/EIA-569-A for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

2. Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA:  A minimum of 5 inches (127 mm).

b. Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 12 inches (300 mm).

c. Electrical Equipment Rating More Than 5 kVA:  A minimum of 24 inches (610 mm).

3. Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA:  A minimum of 2-1/2 inches (64 mm).

b. Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 6 inches (150 mm).

c. Electrical Equipment Rating More Than 5 kVA:  A minimum of 12 inches (300 mm).

4. Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

a. Electrical Equipment Rating Less Than 2 kVA:  No requirement.

b. Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 3 inches (76 mm).

c. Electrical Equipment Rating More Than 5 kVA:  A minimum of 6 inches (150 mm).

5. Separation between Communications Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger:  A minimum of 48 inches (1200 mm).

6. Separation between Communications Cables and Fluorescent Fixtures:  A minimum of 5 inches (127 mm).

3.5 FIRESTOPPING

A. Comply with requirements in Division 07 Section "Penetration Firestopping."

B. Comply with TIA/EIA-569-A, Annex A, "Firestopping."

C. Comply with BICSI TDMM, "Firestopping Systems" Article.

3.6 GROUNDING

A. Install grounding according to BICSI TDMM, "Grounding, Bonding, and Electrical Protection" Chapter.

B. Comply with ANSI-J-STD-607-A.

C. Locate grounding bus bar to minimize the length of bonding conductors.  Fasten to wall allowing at least 2-inch (50-mm) clearance behind the grounding bus bar.  Connect grounding bus bar with a minimum No. 4 AWG grounding electrode conductor from grounding bus bar to suitable electrical building ground.

D. Bond metallic equipment to the grounding bus bar, using not smaller than No. 6 AWG equipment grounding conductor.

3.7 IDENTIFICATION

Retain one of first two paragraphs below.

A. Identify system components, wiring, and cabling complying with TIA/EIA-606-A.  Comply with requirements for identification specified in Division 26 Section "Identification for Electrical Systems."

See Evaluations for discussion about designating the class of cabling plant administration and color-coding of cross-connect fields.

1. Administration Class:  [1] [2] [3] [4].

2. Color-code cross-connect fields.  Apply colors to voice and data service backboards, connections, covers, and labels.

B. Using cable management system software specified in Part 2, develop Cabling Administration Drawings for system identification, testing, and management.  Use unique, alphanumeric designation for each cable and label cable, jacks, connectors, and terminals to which it connects with same designation.  At completion, cable and asset management software shall reflect as-built conditions.

C. Comply with requirements in Division 09 Section "Interior Painting" for painting backboards.  For fire-resistant plywood, do not paint over manufacturer's label.

See Evaluations for discussion about TIA/EIA standard as it applies to this Section.

D. Paint and label colors for equipment identification shall comply with TIA/EIA-606-A for [Class 2] [Class 3] [Class 4] level of administration[, including optional identification requirements of this standard].

E. Cable Schedule:  Post in prominent location in each equipment room and wiring closet.  List incoming and outgoing cables and their designations, origins, and destinations.  Protect with rigid frame and clear plastic cover.  Furnish an electronic copy of final comprehensive schedules for Project.

F. Cabling Administration Drawings:  Show building floor plans with cabling administration-point labeling.  Identify labeling convention and show labels for telecommunications closets, [backbone pathways and cables,] [entrance pathways and cables,] terminal hardware and positions, horizontal cables, work areas and workstation terminal positions, grounding buses and pathways, and equipment grounding conductors.  Follow convention of TIA/EIA-606-A.  Furnish electronic record of all drawings, in software and format selected by Owner.

G. Cable and Wire Identification:

1. Label each cable within 4 inches (100 mm) of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

2. Each wire connected to building-mounted devices is not required to be numbered at device if color of wire is consistent with associated wire connected and numbered within panel or cabinet.

3. Exposed Cables and Cables in Cable Trays and Wire Troughs:  Label each cable at intervals not exceeding 15 feet (4.5 m).

4. Label each terminal strip and screw terminal in each cabinet, rack, or panel.

a. Individually number wiring conductors connected to terminal strips, and identify each cable or wiring group being extended from a panel or cabinet to a building-mounted device shall be identified with name and number of particular device as shown.

b. Label each unit and field within distribution racks and frames.

5. Identification within Connector Fields in Equipment Rooms and Wiring Closets:  Label each connector and each discrete unit of cable-terminating and connecting hardware.  Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

6. Uniquely identify and label work area cables extending from the MUTOA to the work area.  These cables may not exceed the length stated on the MUTOA label.

H. Labels shall be preprinted or computer-printed type with printing area and font color that contrasts with cable jacket color but still complies with requirements in TIA/EIA-606-A.

1. Cables use flexible vinyl or polyester that flex as cables are bent.

3.8 FIELD QUALITY CONTROL

Retain one of first two paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Visually inspect UTP and optical fiber cable jacket materials for NRTL certification markings.  Inspect cabling terminations in communications equipment rooms for compliance with color-coding for pin assignments, and inspect cabling connections for compliance with TIA/EIA-568-B.1.

2. Visually confirm [Category 5e,] [Category 6,] marking of outlets, cover plates, outlet/connectors, and patch panels.

3. Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

4. Test UTP backbone copper cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors.  Test operation of shorting bars in connection blocks.  Test cables after termination but not cross-connection.

a. Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.2.  Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

5. Optical Fiber Cable Tests:

a. Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.1.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

b. Link End-to-End Attenuation Tests:

1) Horizontal and multimode backbone link measurements:  Test at 850 or 1300 nm in 1 direction according to TIA/EIA-526-14-A, Method B, One Reference Jumper.

2) Attenuation test results for backbone links shall be less than 2.0 dB.  Attenuation test results shall be less than that calculated according to equation in TIA/EIA-568-B.1.

6. UTP Performance Tests:

a. Test for each outlet and MUTOA.  Perform the following tests according to TIA/EIA-568-B.1 and TIA/EIA-568-B.2:

1) Wire map.

2) Length (physical vs. electrical, and length requirements).

3) Insertion loss.

4) Near-end crosstalk (NEXT) loss.

5) Power sum near-end crosstalk (PSNEXT) loss.

6) Equal-level far-end crosstalk (ELFEXT).

7) Power sum equal-level far-end crosstalk (PSELFEXT).

8) Return loss.

9) Propagation delay.

10) Delay skew.

7. Optical Fiber Cable Performance Tests:  Perform optical fiber end-to-end link tests according to TIA/EIA-568-B.1 and TIA/EIA-568-B.3.

Retain first subparagraph below when cable is used for broadband closed-circuit television applications.  Revise to suit tests to verify cable performance for other systems using coaxial cable.

8. Coaxial Cable Tests:  Conduct tests according to Division 27 Section "Master Antenna Television System."

Retain first subparagraph below if Owner intends to use Contractor in final testing after its personnel have assumed the operation of communications system.

9. Final Verification Tests:  Perform verification tests for UTP[ and optical fiber] systems after the complete communications cabling and workstation outlet/connectors are installed.

a. Voice Tests:  These tests assume that dial tone service has been installed.  Connect to the network interface device at the demarcation point.  Go off-hook and listen and receive a dial tone.  If a test number is available, make and receive a local, long distance, and digital subscription line telephone call.

b. Data Tests:  These tests assume the Information Technology Staff has a network installed and is available to assist with testing.  Connect to the network interface device at the demarcation point.  Log onto the network to ensure proper connection to the network.

D. Document data for each measurement.  Data for submittals shall be printed in a summary report that is formatted similar to Table 10.1 in BICSI TDMM, or transferred from the instrument to the computer, saved as text files, and printed and submitted.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

E. End-to-end cabling will be considered defective if it does not pass tests and inspections.

F. Prepare test and inspection reports.

3.9 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel in cable-plant management operations, including changing signal pathways for different workstations, rerouting signals in failed cables, and keeping records of cabling assignments and revisions when extending wiring to establish new workstation outlets.[ Include training in cabling administration software.]

END OF SECTION 271500

	COMMUNICATIONS HORIZONTAL CABLING
	271500 - 1



