Copyright 2011 AIA
MasterSpec Professional
02/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 024116 - STRUCTURE DEMOLITION
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Demolition and removal of buildings[ and site improvements].

2. [Abandoning in-place] [Removing] below-grade construction.

3. Disconnecting, capping or sealing, and [abandoning in-place] [removing] site utilities.

4. Salvaging items for reuse by Owner.

1.2 MATERIALS OWNERSHIP

A. Historic items, relics, antiques, and similar objects including, but not limited to, cornerstones and their contents, commemorative plaques and tablets, and other items of interest or value to Owner that may be uncovered during demolition remain the property of Owner.

1. Carefully salvage in a manner to prevent damage and promptly return to Owner.

1.3 INFORMATIONAL SUBMITTALS

A. Proposed Protection Measures: Submit informational report, including Drawings, that indicates the measures proposed for protecting individuals and property[, for environmental protection] [, for dust control] [and] [, for noise control]. Indicate proposed locations and construction of barriers.

1. Adjacent Buildings: Detail special measures proposed to protect adjacent buildings to remain[ including means of egress from those buildings].

B. Schedule of building demolition with starting and ending dates for each activity.

C. Inventory of items to be removed and salvaged.

D. Predemolition [photographs] [or] [video].

E. Statement of Refrigerant Recovery: Signed by refrigerant recovery technician.

1.4 QUALITY ASSURANCE

A. Refrigerant Recovery Technician Qualifications: Certified by EPA-approved certification program.

B. Regulatory Requirements: Comply with governing EPA notification regulations before beginning demolition. Comply with hauling and disposal regulations of authorities having jurisdiction.

C. Standards: Comply with ANSI/ASSE A10.6 and NFPA 241.

D. Predemolition Conference: Conduct conference at [Project site] <Insert location>.

1.5 PROJECT CONDITIONS

A. Buildings to be demolished will be vacated and their use discontinued before start of the Work.

B. Buildings immediately adjacent to demolition area will be occupied. Conduct building demolition so operations of occupied buildings will not be disrupted.

1. Provide not less than [72] <Insert number> hours' notice of activities that will affect operations of adjacent occupied buildings.

2. Maintain access to existing walkways, exits, and other facilities used by occupants of adjacent buildings.

a. Do not close or obstruct walkways, exits, or other facilities used by occupants of adjacent buildings without written permission from authorities having jurisdiction.

C. Owner assumes no responsibility for buildings and structures to be demolished.

1. Conditions existing at time of inspection for bidding purpose will be maintained by Owner as far as practical.

2. Before building demolition, Owner will remove the following items:

a. <Insert items to be removed by Owner>.

Retain first paragraph below, or remove all references to hazardous materials. Insert scope of article to include asbestos, PCBs, and other materials if required. Coordinate statements with the General and Supplementary Conditions. See Evaluations.

D. Hazardous Materials: It is not expected that hazardous materials will be encountered in the Work.

1. Hazardous materials will be removed by Owner before start of the Work.

Retain subparagraph below to cover instances where hazardous materials are unexpectedly found and must be remediated. See the General Conditions for additional requirements on hazardous materials.

2. If materials suspected of containing hazardous materials are encountered, do not disturb; immediately notify Architect and Owner. Hazardous materials will be removed by Owner under a separate contract.

E. On-site storage or sale of removed items or materials is not permitted.

F. Arrange demolition schedule so as not to interfere with [Owner's on-site operations] [or] [operations of adjacent occupied buildings].

PART 2 -  PRODUCTS[ (Not Used)]

Retain "(Not Used)" option in Part 2 title above if deleting "Soil Materials" Article.

Retain article below for backfilling voids that result from demolition operations in below-grade areas. Coordinate with requirements in Part 3.

2.1 SOIL MATERIALS

A. Satisfactory Soils: Comply with requirements in Section 312000 "Earth Moving."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Verify that utilities have been disconnected and capped before starting demolition operations.

B. Inventory and record the condition of items to be removed and salvaged.

Usually retain first option in paragraph below. OSHA regulations require only that a "competent person" perform an engineering survey before building demolition begins. See Evaluations.

C. [Perform] [Engage a professional engineer to perform] an engineering survey of condition of building to determine whether removing any element might result in structural deficiency or unplanned collapse of any portion of structure or adjacent structures during building demolition operations.

3.2 PREPARATION

A. Refrigerant: Remove refrigerant from mechanical equipment according to 40 CFR 82 and regulations of authorities having jurisdiction before starting demolition.

Retain "Existing Utilities" Paragraph below if applicable. Delete if Owner arranges and performs the Work.

B. Existing Utilities: Locate, identify, disconnect, and seal or cap off indicated utilities serving buildings and structures to be demolished.

Retain first subparagraph below if shutting off utilities is responsibility of Owner. Delete if it is responsibility of Contractor.

1. Owner will arrange to shut off indicated utilities when requested by Contractor.

Retain first subparagraph below if shutting off utilities is responsibility of Contractor. Delete if it is responsibility of Owner.

2. Arrange to shut off indicated utilities with utility companies.

3. If removal, relocation, or abandonment of utility services will affect adjacent occupied buildings, then provide temporary utilities that bypass buildings and structures to be demolished and that maintain continuity of service to other buildings and structures.

4. Cut off pipe or conduit a minimum of 24 inches (610 mm) below grade. Cap, valve, or plug and seal remaining portion of pipe or conduit after bypassing according to requirements of authorities having jurisdiction.

5. Do not start demolition work until utility disconnecting and sealing have been completed.

C. Temporary Shoring: Provide and maintain interior and exterior shoring, bracing, or structural support to preserve stability and prevent unexpected movement or collapse of construction being demolished.

D. Salvaged Items:

1. Clean salvaged items of dirt and demolition debris.

2. Pack or crate items after cleaning. Identify contents of containers.

3. Store items in a secure area until delivery to Owner.

4. Transport items to storage area [designated by Owner] [indicated on Drawings].

5. Protect items from damage during transport and storage.

3.3 PROTECTION

A. Existing Facilities: Protect adjacent walkways, loading docks, building entries, and other building facilities during demolition operations. Maintain exits from existing buildings.

B. Existing Utilities: Maintain utility services to remain and protect from damage during demolition operations. Do not interrupt existing utilities serving adjacent occupied or operating facilities unless authorized in writing by Owner and authorities having jurisdiction.

C. Temporary Protection: Erect temporary protection, such as walks, fences, railings, canopies, and covered passageways, where required by authorities having jurisdiction and as indicated. Comply with requirements in Section 015000 "Temporary Facilities and Controls."

1. Protect adjacent buildings and facilities from damage due to demolition activities.

2. Protect existing site improvements, appurtenances, and landscaping to remain.

3. Erect a plainly visible fence around drip line of individual trees or around perimeter drip line of groups of trees to remain.

4. Provide temporary barricades and other protection required to prevent injury to people and damage to adjacent buildings and facilities to remain.

5. Provide protection to ensure safe passage of people around building demolition area and to and from occupied portions of adjacent buildings and structures.

6. Protect walls, windows, roofs, and other adjacent exterior construction that are to remain and that are exposed to building demolition operations.

7. Erect and maintain dustproof partitions and temporary enclosures to limit dust, noise, and dirt migration to occupied portions of adjacent buildings.

D. Remove temporary barriers and protections where hazards no longer exist. Where open excavations or other hazardous conditions remain, leave temporary barriers and protections in place.

3.4 DEMOLITION

A. General: Demolish indicated buildings[ and site improvements] completely. Use methods required to complete the Work within limitations of governing regulations.

1. Do not use cutting torches until work area is cleared of flammable materials. Maintain portable fire-suppression devices during flame-cutting operations.

2. Maintain fire watch during and for at least <Insert number> hours after flame cutting operations.

3. Maintain adequate ventilation when using cutting torches.

4. Locate building demolition equipment and remove debris and materials so as not to impose excessive loads on supporting walls, floors, or framing.

B. Site Access and Temporary Controls: Conduct building demolition and debris-removal operations to ensure minimum interference with roads, streets, walks, walkways, and other adjacent occupied and used facilities.

1. Do not close or obstruct streets, walks, walkways, or other adjacent occupied or used facilities without permission from Owner and authorities having jurisdiction. Provide alternate routes around closed or obstructed traffic ways if required by authorities having jurisdiction.

2. Use water mist and other suitable methods to limit spread of dust and dirt. Comply with governing environmental-protection regulations.

C. Explosives: Use of explosives is not permitted.

D. Proceed with demolition of structural framing members systematically, from higher to lower level. Complete building demolition operations above each floor or tier before disturbing supporting members on the next lower level.

E. Remove debris from elevated portions of the building by chute, hoist, or other device that will convey debris to grade level in a controlled descent.

F. Salvage: Items to be removed and salvaged are indicated [on Drawings.] [below:]

1. <Insert items to be salvaged>.

G. [Demolish] [Abandon] foundation walls and other below-grade construction [within footprint of new construction and extending 5 feet (1.5 m) outside footprint indicated for new construction].

1. Remove below-grade construction, including basements, foundation walls, and footings, [completely] [to at least 6 inches (150 mm) below grade] [to at least 12 inches (300 mm) below grade] [to depths indicated].

H. Existing Utilities: [Demolish] [Abandon] existing utilities and below-grade utility structures [within 5 feet (1.5 m) outside footprint indicated for new construction]. Cut utilities flush with grade.

I. Below-Grade Areas: Completely fill below-grade areas and voids resulting from building demolition operations with [satisfactory soil materials] [recycled pulverized concrete] [recycled pulverized masonry] according to backfill requirements in Section 312000 "Earth Moving."

J. Site Grading: Uniformly rough grade area of demolished construction to a smooth surface, free from irregular surface changes. Provide a smooth transition between adjacent existing grades and new grades.

K. Promptly repair damage to adjacent buildings caused by demolition operations.

3.5 CLEANING

A. Remove demolition waste materials from Project site [and legally dispose of them in an EPA-approved landfill acceptable to authorities having jurisdiction]. See Section 017419 "Construction Waste Management and Disposal" for recycling and disposal of demolition waste.

B. Do not burn demolished materials.

C. Clean adjacent structures and improvements of dust, dirt, and debris caused by building demolition operations. Return adjacent areas to condition existing before building demolition operations began.

END OF SECTION 024116

	STRUCTURE DEMOLITION
	024116 - 1



