Copyright 2011 AIA
MasterSpec Professional
11/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 051213 - ARCHITECTURALLY EXPOSED STRUCTURAL STEEL FRAMING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes architecturally exposed structural-steel (AESS).

1. Requirements in Section 051200 "Structural Steel Framing" also apply to AESS.

1.2 DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

A. AESS: Structural steel designated as "architecturally exposed structural steel" or "AESS" in the Contract Documents.

1.3 PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

A. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

1.4 ACTION SUBMITTALS

A. LEED Submittals:

"Laboratory Test Reports for Credit IEQ 4.2" Subparagraph below applies to LEED for Schools.

1. Laboratory Test Reports for Credit IEQ 4.2: For primers, documentation indicating that products comply with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services') "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

B. Shop Drawings: Show fabrication of AESS components.[ Shop Drawings for structural steel may be used for AESS provided items of AESS are specifically identified and requirements below are met for AESS.]

1. Indicate welds by standard AWS symbols, distinguishing between shop and field welds, and show size, length, and type of each weld. Show backing bars that are to be removed and supplemental fillet welds where backing bars are to remain.[ Indicate grinding, finish, and profile of welds.]

2. Indicate type, size, and length of bolts, distinguishing between shop and field bolts. Identify pretensioned and slip-critical, high-strength bolted connections.[ Indicate orientation of bolt heads.]

Samples required in "Samples" Paragraph below can be used as quality standards in place of mockups.

C. Samples: Submit Samples of AESS to set quality standards for exposed welds.

Two subparagraphs below are examples only. Revise as needed to provide representative examples of required finishing of welded connections.

1. Two steel plates, 3/8 by 8 by 4 inches (9.5 by 200 by 100 mm), with long edges joined by a groove weld[ and with weld ground smooth].

2. Steel plate, 3/8 by 8 by 8 inches (9.5 by 200 by 200 mm), with one end of a short length of rectangular steel tube, 4 by 6 by 3/8 inches (100 by 150 by 9.5 mm), welded to plate with a continuous fillet weld[ and with weld ground smooth and blended].

1.5 QUALITY ASSURANCE

Retain "Fabricator Qualifications" Paragraph below if requirements for fabricator qualifications in this Section exceed those in Section 051200 "Structural Steel Framing." Category STD is for steel building structures; other categories in fabricator certification program are for bridges.

A. Fabricator Qualifications: A qualified fabricator that participates in the AISC Quality Certification Program and is designated an AISC-Certified Plant, Category STD, or is accredited by the IAS Fabricator Inspection Program for Structural Steel (AC 172).

Retain "Installer Qualifications" Paragraph below if requirements for installer qualifications in this Section exceed those in Section 051200 "Structural Steel Framing." Because this is a recently established program, verify availability of certified erectors. Retain category from two options below: ACSE for advanced certified steel erectors, CSE for certified steel erectors.

B. Installer Qualifications: A qualified installer who participates in the AISC Quality Certification Program and is designated an AISC-Certified Erector, [Category ACSE] [Category CSE].

Retain "Shop-Painting Applicators" Paragraph below if requirements for shop-painting applicators in this Section exceed those in Section 051200 "Structural Steel Framing." Qualifications below are usually for high-performance coatings rather than for customary shop priming. Before retaining, verify that fabricators or shop-painting applicators serving Project area are qualified. AISC's program qualifies fabricators as an endorsement to plant certification; SSPC's program usually qualifies paint shops rather than steel fabricators. AISC's Sophisticated Paint Endorsement is based on industry standards and manufacturers' storage, surface preparation, application, and curing requirements; P1 is for enclosed facilities, P2 for covered facilities, and P3 for outside facilities.

C. Shop-Painting Applicators: Qualified according to AISC's Sophisticated Paint [Endorsement P1] [Endorsement P2] [Endorsement P3] or SSPC-QP 3, "Standard Procedure for Evaluating Qualifications of Shop Painting Applicators."

1.6 DELIVERY, STORAGE, AND HANDLING

A. Use special care in handling to prevent twisting, warping, nicking, and other damage. Store materials to permit easy access for inspection and identification. Keep steel members off ground and spaced by using pallets, dunnage, or other supports and spacers. Protect steel members and packaged materials from corrosion and deterioration.

1. Do not store materials on structure in a manner that might cause distortion, damage, or overload to members or supporting structures. Repair or replace damaged materials or structures as directed.

1.7 FIELD CONDITIONS

A. Field Measurements: Where AESS is indicated to fit against other construction, verify actual dimensions by field measurements before fabrication.

PART 2 -  PRODUCTS

2.1 BOLTS, CONNECTORS, AND ANCHORS

Retain this article only for those materials that apply to AESS and are not specified in Section 051200 "Structural Steel Framing."

Tension-control (twist-off) bolt assemblies in "Tension-Control, High-Strength Bolt-Nut-Washer Assemblies" and "Corrosion-Resisting (Weathering Steel), Tension-Control, High-Strength Bolt-Nut-Washer Assemblies" paragraphs below correspond to strength of ASTM A 325 (ASTM A 325M) bolts; retain if round-head bolts are required.

A. Tension-Control, High-Strength Bolt-Nut-Washer Assemblies: ASTM F 1852, Type 1, round-head assemblies, consisting of steel structural bolts with splined ends, heavy-hex carbon-steel nuts, and hardened carbon-steel washers.

Retain one option in "Finish" Subparagraph below.

1. Finish: [Plain] [Mechanically deposited zinc coating].

B. Corrosion-Resisting (Weathering Steel), Tension-Control, High-Strength Bolt-Nut-Washer Assemblies: ASTM F 1852, Type 3, round-head assemblies, consisting of steel structural bolts with splined ends, heavy-hex carbon-steel nuts, and hardened carbon-steel washers.

2.2 FILLER

A. Filler: Polyester filler intended for use in repairing dents in automobile bodies.

2.3 PRIMER

Retain this article only for those materials that apply to AESS and are not retained in Section 051200 "Structural Steel Framing." Insert proprietary primers if required as part of special coating or painting system. Coordinate primer selection with surface preparation and topcoats, requirements for slip-critical joints, and limitations of sprayed fire-resistive materials and intumescent mastic fireproofing. Insert color if required.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools and if primers are fully specified in this Section rather than in the painting Sections.

A. Low-Emitting Materials: Paints and coatings shall comply with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services') "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

B. Primer: Comply with [Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."] [Section 099600 "High-Performance Coatings."] [Section 099113 "Exterior Painting," Section 099123 "Interior Painting," and Section 099600 "High-Performance Coatings."]

C. Etching Cleaner for Galvanized Metal: MPI#25.

D. Galvanizing Repair Paint: [MPI#18, MPI#19, or SSPC-Paint 20] [ASTM A 780/A 780M].

2.4 FABRICATION

A. In addition to special care used to handle and fabricate AESS, comply with the following:

1. Fabricate with exposed surfaces smooth, square, and free of surface blemishes including pitting, rust, scale, and roughness.

2. Grind sheared, punched, and flame-cut edges of AESS to provide smooth surfaces and edges.

3. Fabricate AESS with exposed surfaces free of mill marks.

4. Fabricate AESS with exposed surfaces free of seams to maximum extent possible.

5. Remove blemishes by filling or grinding or by welding and grinding, before cleaning, treating, and shop priming.

6. Fabricate with piece marks fully hidden in the completed structure or made with media that permits full removal after erection.

7. Fabricate AESS to the tolerances specified in AISC 303 for steel that [is] [is not] designated AESS.

8. Seal-weld open ends of hollow structural sections with 3/8-inch (9.5-mm) closure plates.

B. Curved Members: Fabricate indicated members to curved shape by rolling to final shape in fabrication shop.

1. Distortion of webs, stems, outstanding flanges, and legs of angles shall not be visible from a distance of 20 feet (6 m) under any lighting conditions.

2. Tolerances for walls of hollow steel sections after rolling shall be approximately 1/2 inch (13 mm).

C. Coping, Blocking, and Joint Gaps: Maintain uniform gaps of 1/8 inch (3.2 mm) with a tolerance of 1/32 inch (0.8 mm).

Retain option in "Bolt Holes" Paragraph below if permitted. RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts" permits thermally cut bolt holes if approved by engineer of record. Revise standard bolt holes to oversized, short-slotted, or long-slotted bolt holes if permitted and indicate locations of each type on Drawings.

D. Bolt Holes: Cut, drill, [mechanically thermal cut, ]or punch standard bolt holes perpendicular to metal surfaces.

Retain "Cleaning Corrosion-Resisting Structural Steel" Paragraph below for unpainted, corrosion-resisting (weathering) structural steel.

E. Cleaning Corrosion-Resisting Structural Steel: Clean and prepare steel surfaces that are to remain unpainted according to SSPC-SP 6/NACE No. 3, "Commercial Blast Cleaning."

F. Holes: Provide holes required for securing other work to structural steel and for other work to pass through steel members.

Delete option in first subparagraph below if allowing thermally cut holes.

1. Cut, drill, or punch holes perpendicular to steel surfaces.[ Do not thermally cut bolt holes or enlarge holes by burning.]

2. Baseplate Holes: Cut, drill, mechanically thermal cut, or punch holes perpendicular to steel surfaces.

3. Weld threaded nuts to framing and other specialty items indicated to receive other work.

2.5 SHOP CONNECTIONS

A. High-Strength Bolts: Shop install high-strength bolts according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts" for type of bolt and type of joint specified.

RCSC requires that joint types be specified in the Contract Documents for most loading conditions. See Evaluations for a discussion of the joint types in "Joint Type" Subparagraph below, which are the three types RCSC now recognizes. Insert particular bolt pretensioning method for pretensioned or slip-critical joints if required; RCSC states that each type can provide satisfactory results.

1. Joint Type: [Snug tightened] [Pretensioned] [Slip critical].

Retain option in "Weld Connections" Paragraph below for "High-Seismic Applications" as defined in AISC 360.

B. Weld Connections: Comply with AWS D1.1/D1.1M[ and AWS D1.8/D1.8M] for tolerances, appearances, welding procedure specifications, weld quality, and methods used in correcting welding work, and comply with the following:

1. Assemble and weld built-up sections by methods that will maintain true alignment of axes without exceeding specified tolerances.

2. Use weld sizes, fabrication sequence, and equipment for AESS that limit distortions to allowable tolerances.

3. Provide continuous, sealed welds at angle to gusset-plate connections and similar locations where AESS is exposed to weather.

4. Provide continuous welds of uniform size and profile where AESS is welded.

Retain one of first two subparagraphs below.

5. Grind butt and groove welds flush to adjacent surfaces within tolerance of plus 1/16 inch, minus zero inch (plus 1.5 mm, minus zero mm).

6. Make butt and groove welds flush to adjacent surfaces within tolerance of plus 1/16 inch, minus zero inch (plus 1.5 mm, minus zero mm). Do not grind unless required for clearances or for fitting other components, or unless directed to correct unacceptable work.

7. Remove backing bars or runoff tabs; back-gouge and grind steel smooth.

8. At locations where welding on the far side of an exposed connection of AESS occurs, grind distortions and marking of the steel to a smooth profile aligned with adjacent material.

Retain one of two subparagraphs below.

9. Make fillet welds oversize and grind to uniform profile with smooth face and transition.

10. Make fillet welds of uniform size and profile with exposed face smooth and slightly concave. Do not grind unless directed to correct unacceptable work.

2.6 GALVANIZING

Retain this article if galvanizing of AESS is required but not retained in Section 051200 "Structural Steel Framing." Note that hot dip galvanizing may cause some distortion (warpage), especially with small steel members.

A. Hot-Dip Galvanized Finish: Apply zinc coating by the hot-dip process to structural steel according to ASTM A 123/A 123M.

Retain first subparagraph below if galvanized steel is painted.

1. Do not quench or apply post-galvanizing treatments that might interfere with paint adhesion.

2. Fill vent and drain holes that are exposed in the finished Work, unless indicated to remain as weep holes, by plugging with zinc solder and filing off smooth.

Revise locations in subparagraph below where galvanizing is required to suit Project. Subparagraph is an example only; delete and indicate items to be galvanized on Drawings if preferred.

3. Galvanize [lintels] <Insert description> attached to structural-steel frame and located in exterior walls.

2.7 SHOP PRIMING

Retain this article if shop priming is required and is different from that specified in Section 051200 "Structural Steel Framing."

A. Shop prime steel surfaces except the following:

1. Surfaces embedded in concrete or mortar. Extend priming of partially embedded members to a depth of 2 inches (50 mm).

2. Surfaces to be field welded.

3. Surfaces to be high-strength bolted with slip-critical connections.

4. Surfaces to receive sprayed fire-resistive materials.

Retain subparagraph below if galvanized surfaces are not to be shop primed.

5. Galvanized surfaces.

B. Surface Preparation[ for Nongalvanized Steel]:

Retain surface-preparation standards in six subparagraphs below or revise to suit Project. Coordinate minimum surface-preparation requirements with selection of primers, paint, and coating systems. See Evaluations.

Cleaning in first subparagraph below removes loose rust, mill scale, and paint.

1. SSPC-SP 3, "Power Tool Cleaning."

Cleaning in first subparagraph below permits tight residues of rust, mill scale, and coatings to remain.

2. SSPC-SP 7/NACE No. 4, "Brush-off Blast Cleaning."

Cleaning in first subparagraph below exceeds SSPC-SP 7/NACE No. 4 but is less than cleaning specified in SSPC-SP 6/NACE No. 3.

3. SSPC-SP 14/NACE No. 8, "Industrial Blast Cleaning."

Cleaning in first subparagraph below requires complete removal of rust, mill scale, and paint by power tools. SSPC-SP 11 uses nonabrasive methods and bridges the gap between the marginal cleaning required in SSPC-SP 2, SSPC-SP 3, and SSPC-SP 7/NACE No. 4, and the more thorough cleaning required in SSPC-SP 6/NACE No. 3, SSPC-SP 10/NACE No. 2, and SSPC-SP 5/NACE No. 1.

4. SSPC-SP 11, "Power Tool Cleaning to Bare Metal."

Cleaning in first subparagraph below requires that two-thirds of surface area be free of visible residue.

5. SSPC-SP 6/NACE No. 3, "Commercial Blast Cleaning."

Cleaning in subparagraph below requires that 95 percent of surface area be free of visible residue.

6. SSPC-SP 10/NACE No. 2, "Near-White Blast Cleaning."

C. Preparing Galvanized Steel for Shop Priming: After galvanizing, thoroughly clean steel of grease, dirt, oil, flux, and other foreign matter, and treat with etching cleaner.

D. Priming: Immediately after surface preparation, apply primer according to manufacturer's written instructions and at rate recommended by SSPC to provide a minimum dry film thickness of 1.5 mils (0.038 mm). Use priming methods that result in full coverage of joints, corners, edges, and exposed surfaces.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Verify, with steel erector present, elevations of concrete- and masonry-bearing surfaces and locations of anchor rods, bearing plates, and other embedments for compliance with requirements.

1. Prepare a certified survey of bearing surfaces, anchor rods, bearing plates, and other embedments showing dimensions, locations, angles, and elevations.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Provide temporary shores, guys, braces, and other supports during erection to keep AESS secure, plumb, and in alignment.

1. If possible, locate welded tabs for attaching temporary bracing and safety cabling where they will be concealed from view in the completed Work.

3.3 ERECTION

A. Set AESS accurately in locations and to elevations indicated and according to AISC 303 and AISC 360.

1. Erect AESS to the tolerances specified in AISC 303 for steel that [is] [is not] designated AESS.

If thermal cutting is permitted, retain option in paragraph below.

B. Do not use thermal cutting during erection[ unless approved by Architect. Finish thermally cut sections within smoothness limits in AWS D1.1/D1.1M].

3.4 FIELD CONNECTIONS

A. High-Strength Bolts: Install high-strength bolts according to RCSC's "Specification for Structural Joints Using ASTM A 325 or A 490 Bolts" for type of bolt and type of joint specified.

RCSC requires that joint types be specified in the Contract Documents for most loading conditions. See Evaluations for a discussion of the joint types in "Joint Type" Subparagraph below, which are the three types RCSC now recognizes. Insert particular bolt pretensioning method for pretensioned or slip-critical joints if required; RCSC states that each type can provide satisfactory results.

1. Joint Type: [Snug tightened] [Pretensioned] [Slip critical].

2. Orient bolt heads [as indicated on Drawings] [in same direction for each connection and to maximum extent possible in same direction for similar connections].

B. Weld Connections: Comply with requirements in "Weld Connections" Paragraph in "Shop Connections" Article.

1. Remove backing bars or runoff tabs; back-gouge and grind steel smooth.

2. Remove erection bolts, fill holes, and grind smooth.

3. Fill weld access holes and grind smooth.

3.5 FIELD QUALITY CONTROL

Retain "Testing Agency" Paragraph below to identify who shall perform tests and inspections.

A. Testing Agency: Owner will engage a qualified independent testing and inspecting agency to inspect AESS as specified in Section 051200 "Structural Steel Framing." The testing agency is not responsible for enforcing requirements relating to aesthetic effect.

B. Architect will observe AESS in place to determine acceptability relating to aesthetic effect.

3.6 REPAIRS AND PROTECTION

A. Remove welded tabs that were used for attaching temporary bracing and safety cabling and that are exposed to view in the completed Work. Grind steel smooth.

B. Galvanized Surfaces: Clean field welds, bolted connections, and abraded areas and repair galvanizing to comply with ASTM A 780/A 780M.

END OF SECTION 051213

	ARCHITECTURALLY EXPOSED STRUCTURAL STEEL FRAMING
	051213 - 1



