Copyright 2010 AIA
MasterSpec Professional
08/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 074213.19 - INSULATED METAL WALL PANELS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Foamed-insulation-core metal wall panels.

2. Laminated-insulation-core metal wall panels.

1.3 PREINSTALLATION MEETINGS

A. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

1.4 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

1. Product Data for Credit MR 4: For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content. Include statement indicating cost for each product having recycled content.

C. Shop Drawings: Include fabrication and installation layouts of metal panels; details of edge conditions, joints, panel profiles, corners, anchorages, attachment system, trim, flashings, closures, and accessories; and special details.

D. Samples: For each type of metal panel indicated.

1.5 INFORMATIONAL SUBMITTALS

A. Product test reports.

B. Warranties: Samples of special warranties.

1.6 CLOSEOUT SUBMITTALS

A. Maintenance data.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of metal panel systems that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for metal panels.

1. Warranty Period: [Two] <Insert number> years from date of Substantial Completion.

B. Special Warranty on Panel Finishes: Manufacturer's standard form in which manufacturer agrees to repair finish or replace metal panels that show evidence of deterioration of factory-applied finishes within specified warranty period.

Verify available warranties for metal panel finishes and insert number in "Finish Warranty Period" Subparagraph below. A 20-year period is available for fluoropolymer finish and is the maximum included with manufacturers' published data; a 10-year period is usually available for siliconized polyester. Longer periods for premium finishes may be available.

1. Finish Warranty Period: [20] [10] <Insert number> years from date of Substantial Completion.

Insert requirements for special weathertightness warranty if needed. Panel manufacturers do not typically offer such warranties on wall systems.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Recycled Content of Steel Products" Paragraph below to specify recycled content if applying for LEED Credit MR 4. USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation. The Steel Recycling Institute indicates that steel sheet typically has 23 percent postconsumer recycled content and 1.5 percent preconsumer recycled content.

A. Recycled Content of Steel Products: Postconsumer recycled content plus one-half of preconsumer recycled content not less than [25] <Insert number> percent.

B. Structural Performance: Provide metal panel systems capable of withstanding the effects of the following loads, based on testing according to ASTM E 72:

1. Wind Loads: As indicated on Drawings.

2. Other Design Loads: [As indicated on Drawings] <Insert loads>.

3. Deflection Limits: For wind loads, no greater than [1/180] [1/240] <Insert deflection> of the span.

4. <Insert serviceability requirements>.

C. Air Infiltration: Air leakage of not more than 0.06 cfm/sq. ft. (0.3 L/s per sq. m) when tested according to ASTM E 283 at the following test-pressure difference:

Value in first option in "Test-Pressure Difference" Subparagraph below is equivalent to a 25-mph (40-km/h) wind and is ASTM E 283 default. Products tested to value in second option below, equivalent to a 50-mph (80-km/h) wind, are widely available. Revise to suit Project.

1. Test-Pressure Difference: [1.57 lbf/sq. ft. (75 Pa)] [6.24 lbf/sq. ft. (300 Pa)].

ASTM E 331, in "Water Penetration under Static Pressure" Paragraph below, indicates that "water contained within drainage flashings, gutters, and sills is not considered failure."

D. Water Penetration under Static Pressure: No water penetration when tested according to ASTM E 331 at the following test-pressure difference:

Value in first option in "Test-Pressure Difference" Subparagraph below is equivalent to a 34-mph (55-km/h) wind and is ASTM E 331 default. Products tested to value in second option below, equivalent to a 50-mph wind (80-km/h), are widely available. Revise to suit Project.

1. Test-Pressure Difference: [2.86 lbf/sq. ft. (137 Pa)] [6.24 lbf/sq. ft. (300 Pa)].

E. Thermal Movements: Allow for thermal movements from ambient and surface temperature changes by preventing buckling, opening of joints, overstressing of components, failure of joint sealants, failure of connections, and other detrimental effects. Base calculations on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Differential values (for aluminum in particular) in "Temperature Change (Range)" Subparagraph below are suitable for most of the U.S.; revise to suit Project.

1. Temperature Change (Range): [120 deg F (67 deg C), ambient; 180 deg F (100 deg C), material surfaces] <Insert temperature range>.

F. Fire-Test-Response Characteristics: Provide metal wall panels and system components with the following fire-test-response characteristics, as determined by testing identical panels and system components per test method indicated below by UL or another testing and inspecting agency acceptable to authorities having jurisdiction. Identify products with appropriate markings of applicable testing agency.

Subparagraphs below are examples only; revise to suit Project after verifying requirements of authorities having jurisdiction.

Retain "Fire-Resistance Characteristics" Subparagraph below only where fire-resistance-rated wall construction is required and testing has demonstrated that adding insulated wall panels does not reduce fire resistance. Verify acceptability of such assemblies with authorities having jurisdiction.

1. Fire-Resistance Characteristics: Provide materials and construction tested for fire resistance per ASTM E 119.

2. Intermediate-Scale Multistory Fire Test: Tested mockup, representative of completed multistory wall assembly of which wall panel is a part, complies with NFPA 285 for test method and required fire-test-response characteristics of exterior non-load-bearing wall panel assemblies.

3. Radiant Heat Exposure: No ignition when tested according to NFPA 268.

4. Potential Heat: Acceptable level when tested according to NFPA 259.

5. Surface-Burning Characteristics: Provide wall panels with a flame-spread index of 25 or less and a smoke-developed index of 450 or less, per ASTM E 84.

2.2 FOAMED-INSULATION-CORE METAL WALL PANELS

A. General: Provide factory-formed and -assembled metal wall panels fabricated from two metal facing sheets and insulation core foamed in place during fabrication, and with joints between panels designed to form weathertight seals. Include accessories required for weathertight installation.

1. Panel Performance:

a. Flatwise Tensile Strength: 30 psi (207 kPa) when tested according to ASTM C 297/C 297M.

b. Humid Aging: Volume increase not greater than 6.0 percent and no delamination or metal corrosion when tested for seven days at 140 deg F (60 deg C) and 100 percent relative humidity according to ASTM D 2126.

c. Heat Aging: Volume increase not greater than 2.0 percent and no delamination, surface blistering, or permanent bowing when tested for seven days at 200 deg F (93 deg C) according to ASTM D 2126.

d. Cold Aging: Volume decrease not more than 1.0 percent and no delamination, surface blistering, or permanent bowing when tested for seven days at minus 20 deg F (29 deg C) according to ASTM D 2126.

e. Fatigue: No evidence of delamination, core cracking, or permanent bowing when tested to a 20-lbf/sq. ft. (958-kPa) positive and negative wind load and with deflection of L/180 for 2 million cycles.

f. Autoclave: No delamination when exposed to 2-psi (13.8-kPa) pressure at a temperature of 212 deg F (100 deg C) for 2-1/2 hours.

2. Insulation Core: Modified isocyanurate or polyurethane foam using a non-CFC blowing agent, with maximum flame-spread and smoke-developed indexes of 25 and 450, respectively.

a. Closed-Cell Content: 90 percent when tested according to ASTM D 6226.

b. Density: 2.0 to 2.6 lb/cu. ft. (32 to 42 kg/cu. m) when tested according to ASTM D 1622.

c. Compressive Strength: Minimum 20 psi (140 kPa) when tested according to ASTM D 1621.

d. Shear Strength: 26 psi (179 kPa) when tested according to ASTM C 273/C 273M.

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

B. Exposed-Fastener, Foamed-Insulation-Core Metal Wall Panels <Insert drawing designation>: Formed with a raised, trapezoidal major rib at panel edge and two intermediate stiffening ribs symmetrically spaced between major rib and panel edge; designed for lapping side edges of adjacent panels and mechanically attaching to supports using exposed fasteners in side laps.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. IPS - Insulated Panel Systems, an NCI Company; RWP Wall Panel.

b. <Insert manufacturer's name; product name or designation>.

3. Metallic-Coated Steel Sheet: Facings of zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 (Z275) coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 (Class AZM150) coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

a. Nominal Thickness: [0.022 inch (0.56 mm)] [0.028 inch (0.71 mm)] [0.034 inch (0.86 mm)].

b. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

c. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

Retain "Backer Board" Subparagraph below if required. A backer board provides additional impact resistance.

4. Backer Board: On back side of exterior facing.

Retain "Snap-on Batten" Subparagraph below if required. A batten is optional with some manufacturers; verify availability.

5. Snap-on Batten: Same material, finish, and color as exterior facings of wall panels.

6. Panel Coverage: [36 inches (914 mm)] <Insert dimension> nominal.

7. Panel Thickness: [3.0 inches (76 mm)] [4.0 inches (102 mm)] [5.0 inches (127 mm)] <Insert dimension>.

Coordinate R-value in "Thermal-Resistance Value (R-Value)" Subparagraph below with thickness selected in "Panel Thickness" Subparagraph above.

8. Thermal-Resistance Value (R-Value): <Insert R-value> according to ASTM C 1363.

C. Concealed-Fastener, Foamed-Insulation-Core Metal Wall Panels <Insert drawing designation>: Formed with tongue-and-groove panel edges; designed for sequential installation by interlocking panel edges and mechanically attaching panels to supports using concealed clips or fasteners.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. CENTRIA Architectural Systems; [Formawall 1000] [Versapanel] [Versawall].

b. IPS - Insulated Panel Systems, an NCI company; [ESP] [EWP] [RWP] Wall Panel.

c. Kingspan; [AW-200] [AWS-300] [AWS-300] [AWS-400] Series Wall Panel.

d. MBCI, a division of NCI Building Systems, L.P.; TW-100 Wall Panel.

e. Metl-Span LLC; [7.2 Insul-Rib] [CF Architectural] [CF Fluted] [CFI Fluted] [CF Mesa] [CFI Mesa] [CFI Metl-Plank] [CF Striated] [CFI Striated] [CFI-V-Rib] Insulated Metal Wall Panel.

f. <Insert manufacturer's name; product name or designation>.

3. Metallic-Coated Steel Sheet: Facings of zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 (Z275) coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 (Class AZM150) coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

a. Nominal Thickness: [0.022 inch (0.56 mm)] [0.028 inch (0.71 mm)] [0.034 inch (0.86 mm)].

b. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

c. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

Retain "Backer Board" Subparagraph below if required. A backer board provides additional impact resistance.

4. Backer Board: On back side of exterior facing.

Retain "Snap-on Batten" Subparagraph below if required. A batten is an optional feature with some manufacturers; verify availability.

5. Snap-on Batten: Same material, finish, and color as exterior facings of wall panels.

6. Panel Coverage: [36 inches (914 mm)] [40 inches (1016 mm)] <Insert dimension> nominal.

7. Panel Thickness: [1.0 inch (25 mm)] [1.5 inches (38 mm)] [2.0 inches (51 mm)] [2.5 inches (64 mm)] [3.0 inches (76 mm)] [4.0 inches (102 mm)] [5.0 inches (127 mm)] <Insert dimension>.

Coordinate R-value in "Thermal-Resistance Value (R-Value)" Subparagraph below with thickness retained in "Panel Thickness" Subparagraph above.

8. Thermal-Resistance Value (R-Value): <Insert R-value> according to ASTM C 1363.

2.3 LAMINATED-INSULATION-CORE METAL WALL PANELS

A. General: Provide factory-formed and -assembled metal wall panels fabricated from two metal facing sheets and core material laminated or otherwise securely bonded to facing sheets during fabrication without use of contact adhesives, and with joints between panels designed to form weathertight seals. Include accessories required for weathertight installation.

1. Panel Performance:

a. Flatwise Tensile Strength: 27 psi (186 kPa) when tested according to ASTM C 297/C 297M.

b. Humid Aging: Volume increase not greater than 6.0 percent and no delamination or metal corrosion when tested for seven days at 140 deg F (60 deg C) and 100 percent relative humidity according to ASTM D 2126.

c. Heat Aging: Volume increase not greater than 2.0 percent and no delamination, surface blistering, or permanent bowing when tested for seven days at 200 deg F (93 deg C) according to ASTM D 2126.

d. Cold Aging: Volume decrease not more than 1.0 percent and no delamination, surface blistering, or permanent bowing when tested for seven days at minus 20 deg F (29 deg C) according to ASTM D 2126.

e. Fatigue: No evidence of delamination, core cracking, or permanent bowing when tested to a 20-lbf/sq. ft. (958-kPa) positive and negative wind load and with deflection of L/180 for 2 million cycles.

f. Autoclave: No delamination when exposed to 2-psi (13.8-kPa) pressure at a temperature of 212 deg F (100 deg C) for 2-1/2 hours.

B. Wrapped-Edge, Laminated-Insulation-Core Metal Wall Panels <Insert drawing designation>: Formed with flush exterior panel facing wrapped over panel edges; designed for independent installation by mechanically attaching [panels to supports using staggered, concealed side clips engaging panel edges] [through extended panel edges to supports using concealed fasteners]; with [sealant] [gasketed] joints.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Architectural Specialty Products, Inc.; Series 500.

b. Kingspan; Designwall 1000.

c. Protean Construction Products, Inc.; FM-100 Panel.

d. <Insert manufacturer's name; product name or designation>.

3. Metallic-Coated Steel Sheet: Facings of zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 (Z275) coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 (Class AZM150) coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

a. Nominal Thickness: [0.028 inch (0.71 mm)] [0.034 inch (0.86 mm)] [0.040 inch (1.02 mm)] [0.052 inch (1.32 mm)].

b. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

c. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

4. Aluminum Sheet: Fabricate panel with exterior and interior facings of same material and thickness. Provide facings of aluminum coil-coated sheet, ASTM B 209 (ASTM B 209M), alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

a. Thickness: [0.032 inch (0.81 mm)] [0.040 inch (1.02 mm)] [0.050 inch (1.27 mm)] [0.063 inch (1.60 mm)] [0.080 inch (2.03 mm)].

b. Surface: [Smooth, flat] [Embossed] finish.

c. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

d. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

5. Core Material: [Manufacturers' standard.][Board insulation of the following type:]

Retain "Polyisocyanurate Insulation," "Extruded-Polystyrene Board Insulation," or "Molded-Polystyrene Board Insulation" Subparagraph below.

a. Polyisocyanurate Insulation: Closed cell, modified polyisocyanurate foam using a non-CFC blowing agent, board type, with a maximum flame-spread index of 25 and a smoke-developed index of 450.

1) Closed-Cell Content: 90 percent when tested according to ASTM D 6226.

b. Extruded-Polystyrene Board Insulation: ASTM C 578, Type IV, 1.60-lb/cu. ft. (26-kg/cu. m) minimum density, unless otherwise indicated; with a maximum flame-spread index of 25 and a smoke-developed index of 450.

c. Molded-Polystyrene Board Insulation: ASTM C 578, [Type I, 0.9 lb/cu. ft. (14 kg/cu. m)] [Type II, 1.35 lb/cu. ft. (22 kg/cu. m), Class 2 or 3, Grade 3], with a maximum flame-spread index of 25 and a smoke-developed index of 450.

Retain "Backer Board" Subparagraph below if required. A backer board provides additional impact resistance.

6. Backer Board: [0.125-inch- (3-mm-)] [0.250-inch- (6-mm-)] thick hardboard behind exterior facing for increased impact resistance.

Retain steel clips in "Clips" Subparagraph below for steel wall panels; retain stainless-steel clips for aluminum panels.

7. Clips: Manufacturer's standard one piece, formed from [zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet] [stainless steel].

8. Gaskets: Extruded, dry seal silicone.

9. Sealant: Manufacturer's standard silicone.

10. Panel Thickness: [1.0 inch (25 mm)] [2.0 inches (51 mm)] [3.0 inches (76 mm)] [4.0 inches (102 mm)] [5.0 inches (127 mm)] [6.0 inches (152 mm)] <Insert dimension>.

Coordinate R-value in "Thermal-Resistance Value (R-Value)" Subparagraph below with thickness retained in "Panel Thickness" Subparagraph above.

11. Thermal-Resistance Value (R-Value): <Insert R-value> according to ASTM C 1363.

C. Shiplap-Edge, Laminated-Insulation-Core Metal Wall Panels <Insert drawing designation>: Formed with flush exterior panel facing and with shiplap edges; designed for sequential installation by mechanically attaching panels to supports using concealed clips and fasteners; with factory-applied [sealant] [gaskets] in side laps.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Alply LLC; Classic Wall.

b. Architectural Specialty Products, Inc.; Series [HF Vertical] [SCR-DR Horizontal] Preinsulated Metal Siding.

c. Industrial Building Panels, Inc.; 900 Series Thermaply Panels.

d. Kingspan; Designwall [2000] [4000].

e. Protean Construction Products, Inc.; FM-200 Panel.

f. <Insert manufacturer's name; product name or designation>.

3. Metallic-Coated Steel Sheet: Facings of zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 (Z275) coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 (Class AZM150) coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

a. Nominal Thickness: [0.028 inch (0.71 mm)] [0.034 inch (0.86 mm)] [0.040 inch (1.02 mm)].

b. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

c. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

4. Aluminum Sheet: Fabricate panel with exterior and interior facings of same material and thickness. Provide facings of aluminum coil-coated sheet, ASTM B 209 (ASTM B 209M), alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

a. Thickness: [0.032 inch (0.81 mm)] [0.040 inch (1.02 mm)] [0.050 inch (1.27 mm)] [0.063 inch (1.60 mm)].

b. Surface: [Smooth, flat] [Embossed] finish.

c. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

d. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

5. Core Material: [Manufacturers' standard.][Board insulation of the following type:]

Retain "Polyisocyanurate Insulation," "Extruded-Polystyrene Board Insulation," or "Molded-Polystyrene Board Insulation" Subparagraph below.

a. Polyisocyanurate Insulation: Closed cell, modified polyisocyanurate foam using a non-CFC blowing agent, board type, with a maximum flame-spread index of 25 and a smoke-developed index of 450.

1) Closed-Cell Content: 90 percent when tested according to ASTM D 6226.

b. Extruded-Polystyrene Board Insulation: ASTM C 578, Type IV, 1.60-lb/cu. ft. (26-kg/cu. m) minimum density unless otherwise indicated; with a maximum flame-spread index of 25 and a smoke-developed index of 450.

c. Molded-Polystyrene Board Insulation: ASTM C 578, [Type I, 0.9 lb/cu. ft. (14 kg/cu. m)] [Type II, 1.35 lb/cu. ft. (22 kg/cu. m), Class 2 or 3, Grade 3], with a maximum flame-spread index of 25 and a smoke-developed index of 450.

Retain "Backer Board" Subparagraph below if required. A backer board provides additional impact resistance.

6. Backer Board: [0.125-inch- (3-mm-)] [0.250-inch- (6-mm-)] thick hardboard behind exterior facing for increased impact resistance.

Retain steel clips in "Clips" Subparagraph below for steel wall panels; retain stainless-steel clips for aluminum panels.

7. Clips: Manufacturer's standard one piece, formed from [zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet] [stainless steel].

8. Gaskets: Extruded, dry seal silicone.

9. Sealant: Manufacturer's standard silicone.

10. Panel Thickness: [1.0 inch (25 mm)] [2.0 inches (51 mm)] [3.0 inches (76 mm)] [4.0 inches (102 mm)] [5.0 inches (127 mm)] [6.0 inches (152 mm)] <Insert dimension>.

Coordinate R-value in "Thermal-Resistance Value (R-Value)" Subparagraph below with thickness retained in "Panel Thickness" Subparagraph above.

11. Thermal-Resistance Value (R-Value): <Insert R-value> according to ASTM C 1363.

D. Framed-Edge, Laminated-Insulation-Core Metal Wall Panels <Insert drawing designation>: Formed with flush exterior panel facing and integral, extruded edge members; designed for independent installation by mechanically attaching panels to supports through edge framing using concealed fasteners; with gasketed joints.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Alply LLC; Snug-Seam.

b. Architectural Specialty Products, Inc.; Series MLW.

c. Protean Construction Products, Inc.; FM-210 Panel.

d. <Insert manufacturer's name; product name or designation>.

3. Metallic-Coated Steel Sheet: Facings of zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 (Z275) coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 (Class AZM150) coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

a. Nominal Thickness: [0.028 inch (0.71 mm)] [0.034 inch (0.86 mm)] [0.040 inch (1.02 mm)].

b. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

c. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

4. Aluminum Sheet: Fabricate panel with exterior and interior facings of same material and thickness. Provide facings of aluminum coil-coated sheet, ASTM B 209 (ASTM B 209M), alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

a. Thickness: [0.032 inch (0.81 mm)] [0.040 inch (1.02 mm)] [0.050 inch (1.27 mm)] [0.063 inch (1.60 mm)] [0.080 inch (2.03 mm)].

b. Surface: [Smooth, flat] [Embossed] finish.

c. Exterior Finish: [Two-coat fluoropolymer] [Three-coat fluoropolymer] [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

d. Interior Finish: [Siliconized polyester] <Insert finish>.

1) Color: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert color>.

5. Core Material: [Manufacturers' standard.][Board insulation of the following type:]

Retain "Polyisocyanurate Insulation," "Extruded-Polystyrene Board Insulation," or "Molded-Polystyrene Board Insulation" Subparagraph below.

a. Polyisocyanurate Insulation: Closed cell, modified polyisocyanurate foam using a non-CFC blowing agent, board type, with a maximum flame-spread index of 25 and a smoke-developed index of 450.

1) Closed-Cell Content: 90 percent when tested according to ASTM D 6226.

b. Extruded-Polystyrene Board Insulation: ASTM C 578, Type IV, 1.60-lb/cu. ft. (26-kg/cu. m) minimum density unless otherwise indicated; with a maximum flame-spread index of 25 and a smoke-developed index of 450.

c. Molded-Polystyrene Board Insulation: ASTM C 578, [Type I, 0.9 lb/cu. ft. (14 kg/cu. m)] [Type II, 1.35 lb/cu. ft. (22 kg/cu. m), Class 2 or 3, Grade 3], with maximum flame-spread index of 25 and smoke-developed index of 450.

Retain "Backer Board" Subparagraph below if required. A backer board provides additional impact resistance.

6. Backer Board: [0.125-inch- (3-mm-)] [0.250-inch- (6-mm-)] thick hardboard behind exterior facing for increased impact resistance.

7. Edge Members: Extruded aluminum, not less than 0.063-inch (1.60-mm) wall thickness.

8. Gaskets: Extruded, dry seal silicone.

9. Panel Thickness: [1.0 inch (25 mm)] [2.0 inches (51 mm)] [3.0 inches (76 mm)] [4.0 inches (102 mm)] [5.0 inches (127 mm)] [6.0 inches (152 mm)] <Insert dimension>.

Coordinate R-value in "Thermal-Resistance Value (R-Value)" Subparagraph below with thickness retained in "Panel Thickness" Subparagraph above.

10. Thermal-Resistance Value (R-Value): <Insert R-value> according to ASTM C 1363.

2.4 MISCELLANEOUS MATERIALS

A. Miscellaneous Metal Subframing and Furring: ASTM C 645, cold-formed, metallic-coated steel sheet, ASTM A 653/A 653M, G90 (Z275 hot-dip galvanized) coating designation or ASTM A 792/A 792M,Class AZ50 (Class AZM150) aluminum-zinc-alloy coating designation unless otherwise indicated. Provide manufacturer's standard sections as required for support and alignment of metal panel system.

Retain panel accessories, flashing, and trim as required and coordinate with those specified in Section 076200 "Sheet Metal Flashing and Trim."

B. Panel Accessories: Provide components required for a complete, weathertight panel system including trim, copings, fasciae, mullions, sills, corner units, clips, flashings, sealants, gaskets, fillers, closure strips, and similar items. Match material and finish of metal panels unless otherwise indicated.

1. Closures: Provide closures at eaves and rakes, fabricated of same metal as metal panels.

2. Backing Plates: Provide metal backing plates at panel end splices, fabricated from material recommended by manufacturer.

3. Closure Strips: Closed-cell, expanded, cellular, rubber or crosslinked, polyolefin-foam or closed-cell laminated polyethylene; minimum 1-inch- (25-mm-) thick, flexible closure strips; cut or premolded to match metal panel profile. Provide closure strips where indicated or necessary to ensure weathertight construction.

Retain "Backer Board" Paragraph below to provide increased impact resistance. Revise to insert other backer boards such as plywood if required.

C. Backer Board: Hardboard complying with ANSI A135.4, Class 1 tempered, [1/8 inch (3 mm)] [1/4 inch (6 mm)] thick unless otherwise indicated.

D. Flashing and Trim: Provide flashing and trim formed from same material as metal panelsas required to seal against weather and to provide finished appearance. Locations include, but are not limited to, bases, drips, sills, jambs, corners, endwalls, framed openings, rakes, fasciae, parapet caps, soffits, reveals, and fillers. Finish flashing and trim with same finish system as adjacent metal panels.

Insert requirements for explosion-relief panels, including special fasteners, cables, and supports, if required. Verify availability with manufacturers.

E. Panel Fasteners: Self-tapping screws designed to withstand design loads. Provide exposed fasteners with heads matching color of metal panels by means of plastic caps or factory-applied coating. Provide EPDM or PVC sealing washers for exposed fasteners.

F. Panel Sealants: Provide sealant type recommended by manufacturer that are compatible with panel materials, are nonstaining, and do not damage panel finish.

1. Sealant Tape: Pressure-sensitive, 100 percent solids, gray polyisobutylene compound sealant tape with release-paper backing; 1/2 inch (13 mm) wide and 1/8 inch (3 mm) thick.

2. Joint Sealant: ASTM C 920; as recommended in writing by metal panel manufacturer.

3. Butyl-Rubber-Based, Solvent-Release Sealant: ASTM C 1311.

2.5 FABRICATION

A. General: Fabricate and finish metal panels and accessories at the factory, by manufacturer's standard procedures and processes, as necessary to fulfill indicated performance requirements demonstrated by laboratory testing. Comply with indicated profiles and with dimensional and structural requirements.

B. Provide panel profile, including major ribs and intermediate stiffening ribs, if any, for full length of panel.

Retain first paragraph below if gaskets or sealants are factory installed.

C. Fabricate metal panel joints with factory-installed captive gaskets or separator strips that provide a weathertight seal and prevent metal-to-metal contact, and that minimize noise from movements.

D. Sheet Metal Flashing and Trim: Fabricate flashing and trim to comply with manufacturer's recommendations and recommendations in SMACNA's "Architectural Sheet Metal Manual" that apply to design, dimensions, metal, and other characteristics of item indicated.

2.6 FINISHES

A. Panels and Accessories:

Retain one exposed fluoropolymer or siliconized-polyester finish from subparagraphs below. Verify availability of finishes for products specified. If retaining more than one, indicate location of each on Drawings or by inserts. To obtain a proprietary finish system, insert names of coating manufacturers and products. Retain AAMA 621 for steel facings; AAMA 620 for aluminum facings.

1. Two-Coat Fluoropolymer: [AAMA 621] [AAMA 620]. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in color coat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

2. Three-Coat Fluoropolymer: [AAMA 621] [AAMA 620]. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in both color coat and clear topcoat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

3. Siliconized Polyester: Epoxy primer and silicone-modified, polyester-enamel topcoat; with a dry film thickness of not less than 0.2 mil (0.005 mm) for primer and 0.8 mil (0.02 mm) for topcoat.

Finish in "Concealed Finish" Subparagraph below is frequently used as a factory finish for interior surfaces.

4. Concealed Finish: Apply pretreatment and manufacturer's standard white or light-colored acrylic or polyester backer finish consisting of prime coat and wash coat with a minimum total dry film thickness of 0.5 mil (0.013 mm).

PART 3 -  EXECUTION

3.1 PREPARATION

A. Miscellaneous Supports: Install subframing, furring, and other miscellaneous panel support members and anchorages according to ASTM C 754 and metal panel manufacturer's written recommendations.

3.2 INSULATED METAL WALL PANEL INSTALLATION

A. General: Apply continuous ribbon of sealant to panel joint on concealed side of insulated metal wall panels as vapor seal; apply sealant to panel joint on exposed side of panels for weather seal.

1. Fasten foamed-insulation-core metal wall panels to supports with fasteners at each lapped joint at location and spacing and with fasteners recommended by manufacturer.

2. Apply panels and associated items true to line for neat and weathertight enclosure. Avoid "panel creep" or application not true to line.

3. Provide metal-backed washers under heads of exposed fasteners on weather side of insulated metal wall panels.

4. Locate and space exposed fasteners in uniform vertical and horizontal alignment. Use proper tools to obtain controlled uniform compression for positive seal without rupture of washer.

5. Provide sealant tape at lapped joints of insulated metal wall panels and between panels and protruding equipment, vents, and accessories.

6. Apply a continuous ribbon of sealant tape to panel side laps and elsewhere as needed to make panels weathertight.

Retain subparagraph below if required; coordinate with products retained in Part 2.

7. Apply snap-on battens to exposed-fastener, insulated-core metal wall panel seams to conceal fasteners.

B. Foamed-Insulation-Core Metal Wall Panels: Fasten metal wall panels to supports with concealed clips at each joint at location and spacing and with fasteners recommended by manufacturer. Fully engage tongue and groove of adjacent panels.

1. Install clips to supports with self-tapping fasteners.

C. Laminated-Insulation-Core Metal Wall Panels:

Retain one installation method from four subparagraphs below that corresponds to products selected in Part 2.

1. Wrapped-Edge Panels: Mechanically attach wall panels to supports using staggered, concealed side clips engaging wrapped panel edges. Install clips to supports with self-tapping fasteners. Seal joints with [backer rod and sealant] [manufacturer's standard gaskets].

2. Wrapped-Edge Panels: Mechanically attach wall panels through extended edge of panels to supports using self-tapping fasteners. Seal joints with [backer rod and sealant] [manufacturer's standard gaskets].

3. Shiplap-Edge Panels: Mechanically attach wall panels to supports using staggered, concealed side clips engaging tongue-and-groove panel edges. Install clips to supports with self-tapping fasteners.

a. Horizontal Joints: [Maintain reveal joint of consistent width] [Seal joints with backer rod and sealant] [Seal joints with manufacturer's standard gaskets].

b. Vertical Joints: [Maintain reveal joint of consistent width] [Seal joints with backer rod and sealant] [Seal joints with manufacturer's standard gaskets].

4. Framed-Edge Panels: Mechanically attach wall panels through integral, extruded edge members to supports using self-tapping fasteners. Seal joints with manufacturer's standard gaskets.

D. Accessory Installation: Install accessories with positive anchorage to building and weathertight mounting, and provide for thermal expansion. Coordinate installation with flashings and other components.

E. Flashing and Trim: Comply with performance requirements, manufacturer's written installation instructions, and SMACNA's "Architectural Sheet Metal Manual." Provide concealed fasteners where possible, and set units true to line and level. Install work with laps, joints, and seams that are permanently watertight.

3.3 CLEANING

A. Remove temporary protective coverings and strippable films, if any, as metal panels are installed, unless otherwise indicated in manufacturer's written installation instructions. On completion of metal panel installation, clean finished surfaces as recommended by metal panel manufacturer. Maintain in a clean condition during construction.

END OF SECTION 074213.19

	INSULATED METAL WALL PANELS
	074213.19 - 1



