Copyright 2010 AIA
MasterSpec Professional
02/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 083113 - ACCESS DOORS AND FRAMES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Access doors and frames for walls and ceilings.

2. Floor access doors and frames.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

"Samples" Paragraph below assumes manufacturer's standard-size Samples are acceptable. Revise to suit Project.

C. Samples: For each door face material.

D. Schedule: Types, locations, sizes, latching or locking provisions, and other data pertinent to installation.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Fire-Rated Access Doors and Frames" Paragraph below if fire-rated units are included in the Work.

A. Fire-Rated Access Doors and Frames: Units complying with NFPA 80 tested according to the following test method:

Verify test method recognized by authorities having jurisdiction and availability of complying products with manufacturers.

1. NFPA 252 or UL 10B for fire-rated access door assemblies installed vertically.

2. NFPA 288 for fire-rated access door assemblies installed horizontally.

2.2 ACCESS DOORS AND FRAMES FOR WALLS AND CEILINGS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

B. Basis-of-Design Product: Subject to compliance with requirements, provide product indicated or comparable product by one of the following:

1. Access Panel Solutions.

2. Acudor Products, Inc.

3. Alfab, Inc.

4. Babcock-Davis.

5. Cendrex Inc.

6. Elmdor/Stoneman Manufacturing Co.; Div. of Acorn Engineering Co.

7. Jensen Industries; Div. of Broan-Nutone, LLC.

8. J. L. Industries, Inc.; Div. of Activar Construction Products Group.

9. Karp Associates, Inc.

10. Larsen's Manufacturing Company.

11. Maxam Metal Products Limited.

12. Metropolitan Door Industries Corp.

13. MIFAB, Inc.

14. Milcor Inc.

15. Nystrom, Inc.

16. Williams Bros. Corporation of America (The).

17. <Insert manufacturer's name>.

Retain "Basis-of-Design Product" subparagraphs in remainder of this article if retaining "Basis-of-Design Product" Paragraph above.

Retain "Source Limitations" Paragraph below if aesthetics are of primary concern.

C. Source Limitations: Obtain each type of access door and frame from single source from single manufacturer.

For projects with multiple access doors, consider providing a schedule, or distinguish between units by giving each a number designation and creating an additional set of requirements for each variation.

D. Flush Access Doors with Exposed Flanges <Insert drawing designation>:

1. Basis-of-Design Product: [Indicated on Drawings] <Insert manufacturer's name; product name or designation>.

2. Assembly Description: Fabricate door to fit flush to frame. Provide manufacturer's standard-width exposed flange, proportional to door size.

3. Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

4. Door Size: <Insert door size>.

Retain "Uncoated Steel Sheet for Door" or "Metallic-Coated Steel Sheet for Door" Subparagraph below. Thicknesses shown are examples only; revise to suit Project.

5. Uncoated Steel Sheet for Door: [Nominal 0.060 inch (1.52 mm), 16 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

6. Metallic-Coated Steel Sheet for Door: [Nominal 0.064 inch (1.63 mm), 16 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

7. Frame Material: [Same material, thickness, and finish as door] <Insert material, thickness, finish>.

8. Hinges: [Manufacturer's standard] <Insert hinge type>.

9. Hardware: [Latch] [Lock].

E. Flush Access Doors with Concealed Flanges <Insert drawing designation>:

1. Basis-of-Design Product: [Indicated on Drawings] <Insert manufacturer's name; product name or designation>.

2. Assembly Description: Fabricate door to fit flush to frame. Provide frame with [gypsum board] [plaster] beads for concealed flange installation.

3. Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

4. Door Size: <Insert door size>.

Retain "Uncoated Steel Sheet for Door" or "Metallic-Coated Steel Sheet for Door" Subparagraph below. Thicknesses shown are examples only; revise to suit Project.

5. Uncoated Steel Sheet for Door: [Nominal 0.060 inch (1.52 mm), 16 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

6. Metallic-Coated Steel Sheet for Door: [Nominal 0.064 inch (1.63 mm), 16 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

7. Frame Material: [Same material and thickness as door] <Insert material, thickness, finish>.

8. Hinges: [Manufacturer's standard] <Insert hinge type>.

9. Hardware: [Latch] [Lock].

F. Recessed Access Doors <Insert drawing designation>:

1. Basis-of-Design Product: [Indicated on Drawings] <Insert manufacturer's name; product name or designation>.

2. Assembly Description: Fabricate door in the form of a pan recessed [1/2 inch (13 mm)] [5/8 inch (16 mm)] [1 inch (25 mm)] for [gypsum board] [plaster] [acoustical tile] <Insert material> infill. Provide frame with [gypsum board bead for concealed flange] [plaster bead for concealed flange] [no bead for acoustical tile] installation.

3. Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

4. Door Size: <Insert door size>.

Retain "Uncoated Steel Sheet for Door" or "Metallic-Coated Steel Sheet for Door" Subparagraph below. Thicknesses shown are examples only; revise to suit Project.

5. Uncoated Steel Sheet for Door: [Nominal 0.060 inch (1.52 mm), 16 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

6. Metallic-Coated Steel Sheet for Door: [Nominal 0.064 inch (1.63 mm), 16 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

7. Frame Material: [Same material and thickness as door] <Insert material, thickness, finish>.

8. Hinges: [Manufacturer's standard] <Insert hinge type>.

9. Hardware: [Latch] [Lock].

G. Aluminum Flush Access Doors <Insert drawing designation>:

1. Basis-of-Design Product: [Indicated on Drawings] <Insert manufacturer's name; product name or designation>.

2. Assembly Description: Fabricate door to fit flush to frame. Provide manufacturer's standard-width exposed flange, proportional to door size.

3. Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

4. Door Size: <Insert door size>.

5. Aluminum Sheet for Door: [Nominal 0.045 inch (1.15 mm)] <Insert thickness>.

a. Finish: [Mill] [Clear anodic].

6. Frame Material: [Same material, thickness, and finish as door] <Insert material, thickness, finish>.

7. Hinges: [Manufacturer's standard] <Insert hinge type>.

8. Hardware: [Lock] [Latch].

H. Fire-Rated, Flush Access Doors with Exposed Flanges <Insert drawing designation>:

1. Basis-of-Design Product: [Indicated on Drawings] <Insert manufacturer's name; product name or designation>.

2. Assembly Description: Fabricate door to fit flush to frame, with a core of mineral-fiber insulation enclosed in sheet metal. Provide self-latching door with automatic closer and interior latch release. Provide manufacturer's standard-width exposed flange, proportional to door size.

3. Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

4. Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [45 minutes] [1 hour] [1-1/2 hours] [2 hours] [3 hours] <Insert requirement>.

5. Temperature-Rise Rating: [450 deg F (250 deg C) at the end of 30 minutes] [250 deg F (139 deg C) at the end of 30 minutes].

Retain "Uncoated Steel Sheet for Door" or "Metallic-Coated Steel Sheet for Door" Subparagraph below. Thicknesses shown are examples only; revise to suit Project. Uninsulated access doors require thicker steel sheet.

6. Uncoated Steel Sheet for Door: [Nominal 0.036 inch (0.91 mm), 20 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

7. Metallic-Coated Steel Sheet for Door: [Nominal 0.040 inch (1.02 mm), 20 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

8. Frame Material: [Same material, thickness, and finish as door] <Insert material, thickness, finish>.

9. Hinges: [Manufacturer's standard] <Insert hinge type>.

10. Hardware: [Latch] [Lock].

I. Fire-Rated, Flush Access Doors with Concealed Flanges <Insert drawing designation>:

1. Basis-of-Design Product: [Indicated on Drawings] <Insert manufacturer's name; product name or designation>.

2. Assembly Description: Fabricate door to fit flush to frame, with a core of mineral-fiber insulation enclosed in sheet metal. Provide self-latching door with automatic closer and interior latch release. Provide frame with [gypsum board] [plaster] beads for concealed flange installation.

3. Locations: [Wall] [Ceiling] [Wall and ceiling] <Insert location or substrate>.

4. Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [45 minutes] [1 hour] [1-1/2 hours] [2 hours] [3 hours] <Insert requirement>.

5. Temperature-Rise Rating: [450 deg F (250 deg C) at the end of 30 minutes] [250 deg F (139 deg C) at the end of 30 minutes].

Retain "Uncoated Steel Sheet for Door" or "Metallic-Coated Steel Sheet for Door" Subparagraph below. Thicknesses shown are examples only; revise to suit Project.

6. Uncoated Steel Sheet for Door: [Nominal 0.036 inch (0.91 mm), 20 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

7. Metallic-Coated Steel Sheet for Door: [Nominal 0.040 inch (1.02 mm), 20 gage] <Insert thickness>.

a. Finish: [Factory prime] [Factory finish].

8. Frame Material: [Same material, thickness, and finish as door] <Insert material, thickness, finish>.

9. Hinges: [Manufacturer's standard] <Insert hinge type>.

10. Hardware: [Latch] [Lock].

J. Hardware:

Retain "Latch" or "Lock" Subparagraph below. Locks provide greater security than latches.

1. Latch: [Cam latch] [Slam latch] [Self-latching bolt] <Insert latch> operated [by screwdriver] [by knurled knob] [by hex-head wrench] [by pinned-hex-head wrench] [by spanner-head wrench] [by flush key] [by ring turn] [as shown on Drawings] [as indicated in schedule] <Insert operator> [with interior release].

2. Lock: [Cylinder] [Mortise cylinder] [As shown on Drawings] [As indicated in schedule] <Insert lock>.

Delete "Lock Preparation" Subparagraph below if lock is provided by access door manufacturer.

a. Lock Preparation: Prepare door panel to accept cylinder specified in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification)."]

2.3 FLOOR ACCESS DOORS AND FRAMES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

B. Basis-of-Design Product: Subject to compliance with requirements, provide product indicated or comparable product by one of the following:

1. Acudor Products, Inc.

2. Babcock-Davis.

3. Bilco Company (The).

4. Cendrex Inc.

5. Dur-Red Products.

6. Halliday Products.

7. Jensen Industries; Div. of Broan-Nutone, LLC.

8. Karp Associates, Inc.

9. Maxam Metal Products Limited.

10. Metropolitan Door Industries Corp.

11. MIFAB, Inc.

12. Milcor Inc.

13. Nystrom, Inc.

14. U.S.F. Fabrication.

15. Williams Bros. Corporation of America (The).

16. <Insert manufacturer's name>.

C. Floor Doors, General: Equip each door with adjustable counterbalancing springs, heavy-duty hold-open arm that automatically locks door open at 90 degrees, release handle with red vinyl grip that allows for one-handed closure, and recessed lift handle.

See Evaluations for discussion of AASHTO H20.

D. Aluminum Floor Door: [Single] [Double]-leaf opening. Extruded-aluminum angle frame with 1/4-inch- (6.4-mm-) thick, diamond-pattern, aluminum tread plate door; nonwatertight; loading capacity to support [150-lbf/sq. ft. (7.2-kN/sq. m) pedestrian live load] [300-lbf/sq. ft. (14.4-kN/sq. m) pedestrian live load] [AASHTO H20 concentrated wheel load, without impact].

E. Watertight Aluminum Floor Door: [Single] [Double]-leaf opening. Extruded-aluminum gutter frame with NPS 1-1/2 (DN 40) drainage coupling and 1/4-inch- (6.4-mm-) thick, diamond-pattern, aluminum tread plate door; watertight; loading capacity to support [150-lbf/sq. ft. (7.2-kN/sq. m) pedestrian live load] [300-lbf/sq. ft. (14.4-kN/sq. m) pedestrian live load] [AASHTO H20 concentrated wheel load, without impact].

Retain same material for frame and door in "Steel Angle-Frame Floor Door" Paragraph below. Verify availability of thicknesses with manufacturers.

F. Steel Angle-Frame Floor Door: [Single] [Double]-leaf opening. [Prime-painted structural] [Galvanized structural]-steel frame with [3/16- or 1/4-inch- (4.8- or 6.4-mm-)] [3/16-inch- (4.8-mm-)] [1/4-inch- (6.4-mm-)] thick, diamond-pattern, [prime-painted structural] [galvanized structural]-steel tread plate door; nonwatertight; loading capacity to support [150-lbf/sq. ft. (7.2-kN/sq. m) pedestrian live] [300-lbf/sq. ft. (14.4-kN/sq. m) pedestrian live] [AASHTO H20 concentrated wheel] load.

Retain "Fire-Resistance Rating" Subparagraph below for fire-rated steel doors.

1. Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [45 minutes] [1 hour] [1-1/2 hours] [2 hours] [3 hours] <Insert requirement>.

a. Finish: Yellow with wording "FIRE DOOR - DO NOT STORE MATERIALS ON SURFACE."

Retain same material for frame and door in "Watertight Steel Gutter-Frame Floor Door" Paragraph below. Verify availability of thicknesses with manufacturers.

G. Watertight Steel Gutter-Frame Floor Door: [Single] [Double]-leaf opening. [Prime-painted structural] [Galvanized structural]-steel channel frame forming gutter with NPS 1-1/2 (DN 40) drainage coupling and [3/16- or 1/4-inch- (4.8- or 6.4-mm-)] [3/16-inch- (4.8-mm-)] [1/4-inch- (6.4-mm-)] thick, diamond-pattern, [prime-painted structural] [galvanized structural]-steel tread plate door; watertight; loading capacity to support [150-lbf/sq. ft. (7.2-kN/sq. m) pedestrian live] [300-lbf/sq. ft. (14.4-kN/sq. m) pedestrian live] [AASHTO H20 concentrated wheel] load.

Retain "Fire-Resistance Rating" Subparagraph below for fire-rated steel doors.

1. Fire-Resistance Rating: Not less than [that indicated] [that of adjacent construction] [45 minutes] [1 hour] [1-1/2 hours] [2 hours] [3 hours] <Insert requirement>.

a. Finish: Yellow with wording "FIRE DOOR - DO NOT STORE MATERIALS ON SURFACE."

Retain "Hardware" Paragraph below and revise to suit Project.

H. Hardware: Provide the following:

1. Hinges: Heavy-duty, [zinc-coated steel] [aluminum] [stainless-steel] [brass] butt hinges with stainless-steel pins.

2. Latch: Stainless-steel slam latch.

3. Lock: [Staple for a padlock] [Recessed hasp] [Keyed deadbolt lock] [Hasp and staple].

4. Hardware Material: [Manufacturer's standard] [Stainless steel, including latch and lifting mechanism assemblies, hold-open arms, and all brackets, hinges, pins, and fasteners].

I. Insulation: [Fiberglass] [Urethane] with liner pan.

J. Safety Accessories: Safety [chains] [net] [railing].

2.4 MATERIALS

Retain materials in this article or revise to suit Project.

A. Steel Plates, Shapes, and Bars: ASTM A 36/A 36M.

"Rolled-Steel Floor Plate" Paragraph below specifies minimum yield point of 30 ksi (205 MPa); revise if a higher strength is required.

B. Rolled-Steel Floor Plate: ASTM A 786/A 786M, rolled from plate complying with ASTM A 36/A 36M or ASTM A 283/A 283M, Grade C or D.

C. Steel Sheet: Uncoated or electrolytic zinc coated, ASTM A 879/A 879M, with cold-rolled steel sheet substrate complying with ASTM A 1008/A 1008M, Commercial Steel (CS), exposed.

D. Metallic-Coated Steel Sheet: ASTM A 653/A 653M, Commercial Steel (CS), Type B; with minimum G60 (Z180) or A60 (ZF180) metallic coating.

E. Aluminum Extrusions: ASTM B 221 (ASTM B 221M), Alloy 6063-T6.

F. Aluminum-Alloy Rolled Tread Plate: ASTM B 632/B 632M, Alloy 6061-T6.

G. Aluminum Sheet: ASTM B 209 (ASTM B 209M), alloy and temper recommended by aluminum producer and finisher for type of use and finish indicated, and with not less than strength and durability properties of Alloy 5005-H15; with minimum sheet thickness according to ANSI H35.2 (ANSI H35.2M).

H. Frame Anchors: Same type as door face.

I. Inserts, Bolts, and Anchor Fasteners: Hot-dip galvanized steel according to ASTM A 153/A 153M or ASTM F 2329.

2.5 FABRICATION

A. General: Provide access door and frame assemblies manufactured as integral units ready for installation.

B. Metal Surfaces: For metal surfaces exposed to view in the completed Work, provide materials with smooth, flat surfaces without blemishes. Do not use materials with exposed pitting, seam marks, roller marks, rolled trade names, or roughness.

C. Doors and Frames: Grind exposed welds smooth and flush with adjacent surfaces. Furnish attachment devices and fasteners of type required to secure access doors to types of supports indicated.

D. Recessed Access Doors: Form face of panel to provide recess for application of applied finish. Reinforce panel as required to prevent buckling.

Retain subparagraph below for recessed access doors with plaster infill.

1. For recessed doors with plaster infill, provide self-furring expanded metal lath attached to door panel.

E. Latching Mechanisms: Furnish number required to hold doors in flush, smooth plane when closed.

1. For cylinder locks, furnish two keys per lock and key all locks alike.

2. For recessed panel doors, provide access sleeves for each locking device. Furnish plastic grommets and install in holes cut through finish.

Retain "Extruded Aluminum" Paragraph below for aluminum access doors.

F. Extruded Aluminum: After fabrication, apply manufacturer's standard protective coating on aluminum that will come in contact with concrete.

2.6 FINISHES

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

B. Protect mechanical finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

C. Appearance of Finished Work: Noticeable variations in same piece are not acceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

D. Steel and Metallic-Coated-Steel Finishes:

Retain "Factory Prime" or "Factory Finish" Subparagraph below. Factory finishes are typically industrial gray.

1. Factory Prime: Apply manufacturer's standard, fast-curing, lead- and chromate-free, universal primer immediately after surface preparation and pretreatment.

2. Factory Finish: Immediately after cleaning and pretreating, apply manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat, with a minimum dry-film thickness of 1 mil (0.025 mm) for topcoat.

E. Aluminum Finishes:

If retaining more than one finish, indicate location of each on Drawings or by inserts.

1. Mill finish.

Retain one of two options in "Clear Anodic Finish" Subparagraph below. Verify availability with manufacturers.

2. Clear Anodic Finish: AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with manufacturer's written instructions for installing access doors and frames.

B. Install doors flush with adjacent finish surfaces or recessed to receive finish material.

3.2 ADJUSTING

A. Adjust doors and hardware, after installation, for proper operation.

B. Remove and replace doors and frames that are warped, bowed, or otherwise damaged.

Insert Access Door Schedule here if required.

END OF SECTION 083113

	ACCESS DOORS AND FRAMES
	083113 - 1



