Copyright 2011 AIA
MasterSpec Professional
08/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 083313 - COILING COUNTER DOORS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Counter doors.

2. Fire-rated counter doors.

B. Related Requirements:

Retain Sections in subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 055000 "Metal Fabrications" for miscellaneous steel supports.

1.2 ACTION SUBMITTALS

A. Product Data: For each type and size of coiling counter door and accessory.

B. Shop Drawings: For each installation and for special components not dimensioned or detailed in manufacturer's product data.

1. Include points of attachment and their corresponding static and dynamic loads imposed on structure.

Retain first subparagraph below for fire-rated doors.

2. Show locations of controls, locking devices, detectors or replaceable fusible links, and other accessories.

Retain subparagraph below if equipment includes wiring.

3. Include diagrams for power, signal, and control wiring.

C. Samples: For each exposed product and for each color and texture specified.

1.3 CLOSEOUT SUBMITTALS

A. Maintenance data.

1.4 QUALITY ASSURANCE

A. Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer for both installation and maintenance of units required for this Project.

Retain "Fire-Rated Door Assemblies" Paragraph below if applicable. Coiling counter doors are labeled by UL for sizes not exceeding 152 sq. ft. (14 sq. m), with no dimension exceeding 13 feet 6 inches (4.11 m).

B. Fire-Rated Door Assemblies: Assemblies complying with NFPA 80 that are listed and labeled by a qualified testing agency, for fire-protection ratings indicated, based on testing at as close to neutral pressure as possible according to [NFPA 252] [or] [UL 10B].

Retain "Temperature-Rise Limit" Subparagraph below if required. The IBC allows an exception for buildings equipped throughout with fire-suppression sprinklers.

1. Temperature-Rise Limit: [Where indicated] [At exit enclosures and exit passageways], provide doors that have a maximum transmitted temperature end point of not more than 450 deg F (250 deg C) above ambient after 30 minutes of standard fire-test exposure.

2. Smoke Control: [Where indicated] [In corridors and smoke barriers], provide doors that are listed and labeled with the letter "S" on the fire-rating label by a qualified testing agency for smoke- and draft-control based on testing according to UL 1784; with maximum air-leakage rate of 3.0 cfm/sq. ft. (0.01524 cu. m/s x sq. m) of door opening at 0.10-inch wg (24.9 Pa) for both ambient and elevated temperature tests.

Retain "Sound-Control Doors" Paragraph below if acoustically rated doors are required.

C. Sound-Control Doors: Assemblies tested in a laboratory for sound-transmission-loss performance according to ASTM E 90, calculated according to ASTM E 413, and rated for not less than the STC value indicated.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 COUNTER DOOR ASSEMBLY <Insert drawing designation>

Copy this article and re-edit for each non-fire-rated counter-door unit. This article is intended as a guide if Project requires several units of varying sizes, characteristics, and capacities. For each door assembly, retain required options in this article and their related requirements in other Part 2 articles.

Insert number to complete drawing designation for each unit required. Use these designations on Drawings to identify each coiling counter door.

A. Counter Door: Coiling counter door formed with curtain of interlocking metal slats.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ACME Rolling Doors.

b. Alpine Overhead Doors, Inc.

c. Alumatec Pacific Products.

d. Amarr Garage Doors.

e. C.H.I. Overhead Doors.

f. City-Gates.

g. Clopay Building Products.

h. Cookson Company.

i. Cornell Iron Works, Inc.

j. Lawrence Roll-Up Doors, Inc.

k. McKeon Rolling Steel Door Company, Inc.

l. Metro Door.

m. Overhead Door Corporation.

n. QMI Security Solutions.

o. Raynor.

p. Wayne-Dalton Corp.

q. <Insert manufacturer's name>.

Retain one of five options in "Operation Cycles" Paragraph below. First option is standard with some manufacturers; second option is more commonly used. Last three options are for high-cycle operation, corrosive environments, and severe or abusive use.

B. Operation Cycles: Door components and operators capable of operating for not less than [10,000] [20,000] [50,000] [100,000] [200,000] <Insert number>.

Retain "STC Rating" Paragraph below for acoustically insulated doors. STC rating of 26 is available from Cornell. Verify availability with other manufacturers.

C. STC Rating: [26] <Insert value>.

D. Door Curtain Material: [Galvanized steel] [Stainless steel] [Aluminum].

Slat profile and sizes in "Door Curtain Slats" Paragraph below vary among manufacturers. Revise size to a range if exact size is not important. Curved slats are not insulated.

E. Door Curtain Slats: [Curved] [Flat] profile slats of [1-1/4-inch (32-mm)] [1-1/2-inch (38-mm)] <Insert dimension> center-to-center height.

1. Perforated Slats: Approximately [1/16-inch (1.6-mm) pinholes] [3/32-inch (2.4-mm) pinholes] [7/8-inch- (22-mm-) wide by 3/8-inch- (10-mm-) high slots] <Insert dimensions>.

2. Fenestrated Slats: Approximately [3- by 5/8-inch (76- by 16-mm)] [4- by 5/8-inch (102- by 16-mm)] [10- by 1-5/8-inch (254- by 41-mm)] <Insert dimensions> openings spaced approximately [1-1/2 inches (38 mm)] <Insert dimension> apart and beginning 12 inches (305 mm) from jamb guides.

3. Vision Panels: Approximately 10- by 1-5/8-inch (254- by 41-mm) openings spaced approximately 2 inches (51 mm) apart and beginning 12 inches (305 mm) from end guides; in [two] [three] <Insert number> rows of slats at height indicated on Drawings; installed with vision-panel glazing.

4. Insulated-Slat Interior Facing: [Metal] [Plastic].

F. Bottom Bar: Manufacturer's standard continuous channel or tubular shape, fabricated [hot-dip galvanized steel] [stainless steel] [or] [aluminum extrusion] and finished [to match door] <Insert requirement>.

G. Curtain Jamb Guides: [Galvanized steel] [Stainless steel] [Aluminum] with exposed finish matching curtain slats.[ Provide continuous integral wear strips to prevent metal-to-metal contact and to minimize operational noise.][ Provide removable post(s) and jamb guides where shown on Drawings.]

Retain "Hood" or "Integral Frame, Hood, and Fascia" Paragraph below.

H. Hood: [Match curtain material and finish] [Galvanized steel] [Stainless steel] [Aluminum].

1. Mounting: [Face of wall] [Between jambs] [As shown on Drawings].

I. Integral Frame, Hood, and Fascia: [Galvanized] [Stainless] steel.

1. Mounting: [Face of wall] [Between jambs] [As shown on Drawings].

J. Sill Configuration: [No sill] [Integral metal sill].

Retain one of first two options in "Locking Devices" Paragraph below. Retain last option for chain-hoist-operated doors or emergency chain-hoist operation.

K. Locking Devices: Equip door with [slide bolt for padlock] [locking device assembly] [and] [chain lock keeper].

Retain "Locking Device Assembly" Subparagraph below if retaining "locking device assembly" option in "Locking Devices" Paragraph above.

1. Locking Device Assembly: [Single-jamb side] [Cremone type, both jamb sides] locking bars, operable from [inside with thumb turn] [outside with cylinder] [outside only, with cylinder] [inside and outside with cylinders] <Insert requirement>.

Retain "Manual Door Operator" or "Electric Door Operator" Paragraph below.

L. Manual Door Operator: [Push-up operation] [Chain-hoist operator] [Manufacturer's standard crank operator] [Awning-crank operator].

M. Electric Door Operator:

Retain one of four options in "Usage Classification" Subparagraph below or revise to suit Project. Usage classification varies among manufacturers and for each operator design; it is a durability requirement separate from whole-door "operation cycles."

1. Usage Classification: [Heavy duty, 25 or more cycles per hour and over 90 cycles per day] [Standard duty, up to 25 cycles per hour and up to 90 cycles per day] [Medium duty, up to 12 cycles per hour and up to 50 cycles per day] [Light duty, up to 10 cycles per hour] <Insert classification>.

Retain one of two options in "Motor Exposure" Subparagraph below or revise to suit Project.

2. Motor Exposure: [Interior] [Exterior, wet, and humid].

3. Emergency Manual Operation: [Push-up] [Chain] [Crank] type.

4. Obstruction-Detection Device: Automatic [photoelectric sensor] [electric sensor edge on bottom bar] [pneumatic sensor edge on bottom bar] [; self-monitoring type] <Insert type>.

Indicate on Drawings which side of door is exterior face if it is not obvious.

5. Control Station(s): [Interior-side mounted] [Exterior-side-mounted] [Where shown on Drawings] <Insert location>.

N. Curtain Accessories: Equip door with [smoke seals] [weatherseals] [astragal] [push/pull handles] [pull-down strap] [poll hook] [and] [automatic closing device] <Insert item>.

O. Door Finish:

Retain one of first four subparagraphs below. These include advertised materials and finishes; available materials and finishes vary with each manufacturer.

Second option in "Aluminum Finish" Subparagraph below is standard.

1. Aluminum Finish: [Mill] [Clear anodized] [Light bronze anodized] [Medium bronze anodized] [Dark bronze anodized] [Black anodized] [Anodized color matching Architect's sample] [Anodized color as selected by Architect from full range of industry colors and color densities] <Insert color>.

2. Baked-Enamel or Powder-Coated Finish: [Color as indicated by manufacturer's designations] [Color matching Architect's sample] [Color as selected by Architect from manufacturer's full range] <Insert color>.

3. Factory Prime Finish: Manufacturer's standard color.

Second option in "Stainless-Steel Finish" Subparagraph below is standard.

4. Stainless-Steel Finish: [No. 2B (bright, cold rolled)] [No. 4 (polished directional satin)] <Insert finish>.

Retain "Interior Curtain-Slat Facing" Subparagraph below for insulated door curtains. Indicate on Drawings which side of door is exterior face if it is not obvious.

5. Interior Curtain-Slat Facing: [Match finish of exterior curtain-slat face] [PVC plastic] <Insert finish>.

2.2 FIRE-RATED COUNTER DOOR ASSEMBLY <Insert drawing designation>

Copy this article and re-edit for each fire-rated counter-door unit. This article is intended as a guide if Project requires several units of varying sizes, characteristics, and capacities. For each door assembly, retain required options in this article and their related requirements in other Part 2 articles.

Insert number to complete drawing designation for each unit required. Use these designations on Drawings to identify each coiling counter door.

A. Fire-Rated Counter Door: Overhead fire-rated coiling door formed with curtain of interlocking metal slats.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ACME Rolling Doors.

b. Alpine Overhead Doors, Inc.

c. Amarr Garage Doors.

d. C.H.I. Overhead Doors.

e. City-Gates.

f. Clopay Building Products.

g. Cookson Company.

h. Cornell Iron Works, Inc.

i. Lawrence Roll-Up Doors, Inc.

j. McKeon Rolling Steel Door Company, Inc.

k. Overhead Door Corporation.

l. Raynor.

m. Wayne-Dalton Corp.

n. <Insert manufacturer's name>.

Retain one of five options in "Operation Cycles" Paragraph below. First option is standard with some manufacturers; second option is more commonly used. Last three options are for high-cycle operation, corrosive environments, and severe or abusive use.

B. Operation Cycles: Door components and operators capable of operating for not less than [10,000] [20,000] [50,000] [100,000] [200,000] <Insert number>.

Verify availability of temperature-rise limit option in "Fire Rating" Paragraph below before retaining. This is required by codes by codes for some locations.

C. Fire Rating: [3/4 hour] [1 hour] [1-1/2 hours] [3 hours] [4 hours] [with temperature-rise limit] [and] [with smoke control].

Retain "STC Rating" Paragraph below for acoustically insulated fire-rated doors. STC rating of 27 is available from McKeon. Verify availability with other manufacturers.

D. STC Rating: [27] <Insert value>.

E. Door Curtain Material: [Galvanized] [Stainless] steel.

Slat profile and sizes in "Door Curtain Slats" Paragraph below vary among manufacturers. Revise size to a range if exact size is not important. Curved slats are not insulated.

F. Door Curtain Slats: [Curved] [Flat] profile slats of [1-1/4-inch (32-mm)] [1-1/2-inch (38-mm)] <Insert dimension> center-to-center height.

1. Vision Panels: Approximately 10- by 1-5/8-inch (254- by 41-mm) openings spaced approximately 2 inches (51 mm) apart and beginning 12 inches (305 mm) from end guides; in [two] [three] <Insert number> rows of slats at height indicated on Drawings; installed with fire-rated vision-panel glazing.

2. Insulated-Slat Interior Facing: Metal.

G. Curtain Jamb Guides: [Galvanized] [Stainless] steel with exposed finish matching curtain slats.

Retain "Hood" or "Integral Frame, Hood, and Fascia" Paragraph below.

H. Hood: [Match curtain material and finish] [Galvanized steel] [Stainless steel].

1. Mounting: [Face of wall] [Between jambs] [As shown on Drawings].

I. Integral Frame, Hood, and Fascia: [Galvanized] [Stainless] steel.

1. Mounting: [Face of wall] [Between jambs] [As shown on Drawings].

J. Sill Configuration: [No sill] [Integral metal sill] [Fire-rated, laminate counter].

Retain one of first two options in "Locking Devices" Paragraph below. Retain last option for chain-hoist-operated doors or emergency chain-hoist operation.

K. Locking Devices: Equip door with [slide bolt for padlock] [locking device assembly] [and] [chain lock keeper].

Retain "Locking Device Assembly" Subparagraph below if retaining "locking device assembly" option in "Locking Devices" Paragraph above.

1. Locking Device Assembly: [Single-jamb side] [Cremone type, both jamb sides] locking bars, operable from [inside with thumbturn] [outside with cylinder] [outside only, with cylinder] [inside and outside with cylinders] <Insert requirement>.

Retain "Manual Door Operator" or "Electric Door Operator" Paragraph below.

L. Manual Door Operator: [Push-up operation] [Chain-hoist operator] [Manufacturer's standard crank operator] [Awning-crank operator].

M. Electric Door Operator:

Retain one of four options in "Usage Classification" Subparagraph below or revise to suit Project. Usage classification varies among manufacturers and for each operator design; it is a durability requirement separate from whole-door "operation cycles."

1. Usage Classification: [Heavy duty, 25 or more cycles per hour and over 90 cycles per day] [Standard duty, up to 25 cycles per hour and up to 90 cycles per day] [Medium duty, up to 12 cycles per hour and up to 50 cycles per day] [Light duty, up to 10 cycles per hour] <Insert classification>.

Retain one of two options in "Motor Exposure" Subparagraph below or revise to suit Project.

2. Motor Exposure: [Interior] [Exterior, wet, and humid].

3. Emergency Manual Operation: [Push-up] [Chain] [Crank] type.

Retain "Obstruction-Detection Device" Subparagraph below if door is used as an automatic garage door.

4. Obstruction Detection Device: Automatic [photoelectric sensor] [electric sensor edge on bottom bar] [pneumatic sensor edge on bottom bar] [; self-monitoring type] <Insert type>.

Indicate on Drawings which side of door is exterior face if it is not obvious.

5. Control Station(s): [Interior-side mounted] [Exterior-side mounted] [Where shown on Drawings] <Insert location>.

N. Curtain Accessories: Equip door with smoke seals, automatic closing device, [astragal] [push/pull handles] [pull-down strap] [poll hook] [and] <Insert item>.

O. Door Finish:

Retain one of first three subparagraphs below. These include advertised materials and finishes; available materials and finishes vary with each manufacturer.

1. Baked-Enamel or Powder-Coated Finish: [Color as indicated by manufacturer's designations] [Color matching Architect's sample] [Color as selected by Architect from manufacturer's full range] <Insert color>.

2. Factory Prime Finish: Manufacturer's standard color.

Second option in "Stainless-Steel Finish" Subparagraph below is standard.

3. Stainless-Steel Finish: [No. 2B (bright, cold rolled)] [No. 4 (polished directional satin)] <Insert finish>.

Retain "Interior Curtain-Slat Facing" Subparagraph below for insulated door curtains. Indicate on Drawings which side of door is exterior face if it is not obvious.

4. Interior Curtain-Slat Facing: [Match finish of exterior curtain-slat face] <Insert finish>.

2.3 MATERIALS, GENERAL

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.4 DOOR CURTAIN MATERIALS AND CONSTRUCTION

A. Door Curtains: Fabricate coiling counter-door curtain of interlocking metal slats in a continuous length for width of door without splices. Unless otherwise indicated, provide slats of thickness and mechanical properties recommended by door manufacturer for performance, size, and type of door indicated, and as follows:

1. Vision-Panel Glazing: Manufacturer's standard clear glazing, fabricated from transparent acrylic sheet or fire-protection rated glass as required for type of door; set in glazing channel secured to curtain slats.

Retain "Insulation," "Metal Interior Curtain-Slat Facing," and "Plastic Interior Curtain-Slat Facing" subparagraphs below as required for acoustically insulated doors; revise to suit Project.

2. Insulation: Fill slats for insulated doors with manufacturer's standard thermal insulation complying with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, according to ASTM E 84 or UL 723. Enclose insulation completely within slat faces.

Indicate on Drawings which side of door is exterior face if it is not obvious.

3. Metal Interior Curtain-Slat Facing: Match metal of exterior curtain-slat face.

"Plastic Interior Curtain-Slat Facing" Subparagraph below is not applicable to fire-rated assemblies.

4. Plastic Interior Curtain-Slat Facing: Extruded PVC plastic with maximum flame-spread index of [25] [75] [200] and smoke-developed index of 450, according to ASTM E 84 or UL 723.

B. Curtain Jamb Guides: Manufacturer's standard angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading. Slot bolt holes for guide adjustment. Provide removable stops on guides to prevent overtravel of curtain.

Retain "Removable Posts and Jamb Guides" Subparagraph below for removable post and guides separating multiple counter-door installations that require a clear opening.

1. Removable Posts and Jamb Guides: Manufacturer's standard.

2.5 HOODS

A. General: Form sheet metal hood to entirely enclose coiled curtain and operating mechanism at opening head. Contour to fit end brackets to which hood is attached. Roll and reinforce top and bottom edges for stiffness. Form closed ends for surface-mounted hoods and fascia for any portion of between-jamb mounting that projects beyond wall face. Equip hood with intermediate support brackets as required to prevent sagging.

1. Include automatic drop baffle on fire-rated doors to guard against passage of smoke or flame.

Item described in "Integral Frame, Hood, and Fascia" Paragraph below is available from some manufacturers for counter doors or fire-rated counter doors; sill is optional.

B. Integral Frame, Hood, and Fascia: Welded [galvanized-steel] [stainless-steel] sheet metal assembly of the following sheet metal(s):

2.6 LOCKING DEVICES

Retain one of or both "Slide Bolt" and "Locking Device Assembly" paragraphs below for required locking device(s); revise to suit Project. First paragraph is standard for push-up doors; revise if no padlock is required or if manufacturer's standard is a bolt on one side. Second paragraph describes a locking device with choice of locations and operation as retained in counter door assembly articles in Part 2.

A. Slide Bolt: Fabricate with side-locking bolts to engage through slots in tracks for locking by padlock, located on both left and right jamb sides, operable from coil side.

B. Locking Device Assembly: Fabricate with cylinder lock, spring-loaded dead bolt, operating handle, cam plate, and adjustable locking bars to engage through slots in tracks.

Retain one of first three options in "Lock Cylinders" Subparagraph below.

1. Lock Cylinders: Cylinders [specified in Section 087100 "Door Hardware"] [specified in Section 087111 "Door Hardware (Descriptive Specification)"] [standard with manufacturer] [and keyed to building keying system].

Retain "Keys" Subparagraph below if cylinders are provided by door manufacturer.

2. Keys: [Two] [Three] <Insert number> for each cylinder.

Retain "Chain Lock Keeper" Paragraph below for chain-hoist-operated doors or emergency chain-hoist operation.

C. Chain Lock Keeper: Suitable for padlock.

D. Safety Interlock Switch: Equip power-operated doors with safety interlock switch to disengage power supply when door is locked.

2.7 CURTAIN ACCESSORIES

A. Smoke Seals: Equip each fire-rated door with replaceable smoke-seal perimeter gaskets or brushes for smoke and draft control as required for door listing and labeling by a qualified testing agency.

B. Astragal: Equip each door bottom bar with a replaceable, adjustable, continuous, compressible gasket of flexible vinyl, rubber, or neoprene as a cushion bumper.

C. Push/Pull Handles: Equip each push-up-operated or emergency-operated door with lifting handles on each side of door, finished to match door.

Retain "Pull-Down Strap" or "Poll Hooks" Paragraph below if required.

D. Pull-Down Strap: Provide pull-down straps for doors more than 84 inches (2130 mm) high.

E. Poll Hooks: Provide pole hooks and poles for doors more than 84 inches (2130 mm) high.

F. Automatic-Closing Device: Equip each fire-rated door with an automatic-closing device or holder-release mechanism and governor unit complying with NFPA 80 and an easily tested and reset release mechanism. Automatic-closing device shall be designed for activation by the following:

Retain one or more of four subparagraphs below and insert others if required to suit Project. If more than one type of activation (or combination) is required, identify primary and secondary closing devices.

Retain first subparagraph below to comply with NFPA 80 requirement for fusible links on both sides of door opening. Revise if not required on both sides of door opening or to add fusible-link ceiling unit for use with suspended ceilings.

1. Replaceable fusible links with temperature rise and melting point of [165 deg F (74 deg C)] <Insert temperature> interconnected and mounted on both sides of door opening.

2. Manufacturer's standard UL-labeled smoke detector and door-holder-release devices.

3. Manufacturer's standard UL-labeled heat detector and door-holder-release devices.

4. Building fire-detection, smoke-detection, and -alarm systems.

2.8 COUNTER DOOR ACCESSORIES

Retain "Integral Metal Sill" Paragraph below if required.

A. Integral Metal Sill: Fabricate sills as integral part of frame assembly of Type 304 stainless steel in manufacturer's standard thickness with [No. 4] <Insert finish> finish.

Product in "Fire-Rated, Laminate Counter" Paragraph below may be specified for interior openings in lieu of integral sheet-metal sills.

B. Fire-Rated, Laminate Counter: Fire-door manufacturer's high-pressure decorative laminate-covered countertop, UL or ITS tested and labeled for 1-1/2-hour fire rating for approved use with fire-door assembly.

2.9 COUNTERBALANCING MECHANISM

A. General: Counterbalance doors by means of manufacturer's standard mechanism with an adjustable-tension, steel helical torsion spring mounted around a steel shaft and contained in a spring barrel connected to top of curtain with barrel rings. Use grease-sealed bearings or self-lubricating graphite bearings for rotating members.

B. Brackets: Manufacturer's standard mounting brackets of either cast iron or cold-rolled steel plate.

2.10 MANUAL DOOR OPERATORS

Retain this article for manually operated doors, not including emergency manual operation for electric door operators.

A. General: Equip door with manual door operator by door manufacturer.

B. Push-up Door Operation: Design counterbalance mechanism so that required lift or pull for door operation does not exceed [25 lbf (111 N)] <Insert value>.

C. Chain-Hoist Operator: Consisting of endless steel hand chain, chain-pocket wheel and guard, and gear-reduction unit with a maximum [25-lbf (111-N)] [30-lbf (133-N)] <Insert value> force for door operation. Provide alloy-steel hand chain with chain holder secured to operator guide.

"Awning" and "box" are the two types of crank operators. Indicate required type in door assembly articles retained in Part 2.

D. Crank Operator: Consisting of crank and crank gearbox, steel crank drive shaft, and gear-reduction unit, of type indicated. Size gears to require not more than [25-lbf (111-N)] [30-lbf (133-N)] <Insert value> force to turn crank. Fabricate gearbox to be oil tight and to completely enclose operating mechanism. Provide manufacturer's standard crank-locking device.

2.11 ELECTRIC DOOR OPERATORS

Retain this article for electric door operators, including emergency manual operation, and for larger units and remotely controlled or frequently operated doors. Coordinate with Project's electrical engineer for interface of electric door operators and equipment with fire-protection system.

A. General: Electric door operator assembly of size and capacity recommended and provided by door manufacturer for door and operation-cycles requirement specified, with electric motor and factory-prewired motor controls, starter, gear-reduction unit, solenoid-operated brake, clutch, control stations, control devices, integral gearing for locking door, and accessories required for proper operation.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Specific operators may not be available from all door manufacturers; operator features may not be common to all operator manufacturers. Consult door and operator manufacturers for recommendations.

a. Chamberlain Group, Inc. (The).

b. <Insert manufacturer's name>.

3. Comply with NFPA 70.

4. Control equipment complying with NEMA ICS 1, NEMA ICS 2, and NEMA ICS 6, with NFPA 70 Class 2 control circuit, maximum 24-V ac or dc.

Durability requirement in "Usage Classification" Paragraph below is separate from "operation cycles," which apply to the whole door system.

B. Usage Classification: Electric operator and components capable of operating for not less than number of cycles per hour indicated for each door.

Retain option in "Motors" Paragraph below unless external controller (disconnect switch) is indicated on Drawings. Coordinate with Project's electrical engineer.

C. Motors: Reversible-type motor[ with controller (disconnect switch)] for motor exposure indicated.

1. Electrical Characteristics:

Retain one of two options in "Phase" Subparagraph below based on required motor size. Verify motor performance and availability with door manufacturer and coordinate electrical characteristics with Project's electrical engineer. See Evaluations.

a. Phase: [Single phase] [Polyphase].

b. Volts: [115] [208] [230] [460] <Insert value> V.

c. Hertz: 60.

Speed in "Motor Size" Subparagraph below is for standard-speed doors.

2. Motor Size: Minimum size as indicated. If not indicated, large enough to start, accelerate, and operate door in either direction from any position, at a speed not less than 8 in./sec. (203 mm/s) and not more than 12 in./sec. (305 mm/s), without exceeding nameplate ratings or service factor.

Revise "Operating Controls, Controllers, Disconnect Switches, Wiring Devices, and Wiring" Subparagraph below if required; coordinate requirements with Project's electrical engineer.

3. Operating Controls, Controllers, Disconnect Switches, Wiring Devices, and Wiring: Manufacturer's standard unless otherwise indicated.

Retain "Obstruction Detection Devices" Paragraph below if required; revise if required for fire-rated door applications according to requirements of authorities having jurisdiction.

D. Obstruction Detection Devices: External entrapment protection consisting of indicated automatic safety sensor capable of protecting full width of door opening.[ For non-fire-rated doors, activation of device immediately stops and reverses downward door travel.][ For fire-rated doors, activation delays closing.]

Retain "Photoelectric Sensor" or "Electric Sensor Edge" Subparagraph below, or both, to suit Project.

1. Photoelectric Sensor: Manufacturer's standard system designed to detect an obstruction in door opening without contact between door and obstruction.

Retain "Self-Monitoring Type" Subparagraph below if required.

a. Self-Monitoring Type: Designed to interface with door operator control circuit to detect damage to or disconnection of sensing device. When self-monitoring feature is activated, door closes only with sustained or constant pressure on close button.

2. Electric Sensor Edge: Automatic safety sensor edge, located within astragal mounted to bottom bar. Contact with sensor activates device. Connect to control circuit using manufacturer's standard take-up reel or self-coiling cable.

Retain "Self-Monitoring Type" Subparagraph below if required.

a. Self-Monitoring Type: Four-wire configured device designed to interface with door operator control circuit to detect damage to or disconnection of sensor edge.

Device in "Pneumatic Sensor Edge" Subparagraph below may be limited to a width of 18 feet (5.5 m); verify availability with manufacturer.

3. Pneumatic Sensor Edge: Automatic safety sensor edge, located within astragal mounted to bottom bar. Contact with sensor activates device.

Retain "Control Station" Paragraph for control stations in fixed locations. A sustained- or constant-pressure (in lieu of a momentary-contact) switch may also be required for opening cycles according to authorities having jurisdiction; revise requirements and counter door assembly articles retained in Part 2 as needed.

E. Control Station: Three-button control station in fixed location with momentary-contact push-button controls labeled "Open" and "Stop" and sustained- or constant-pressure push-button control labeled "Close."

1. Type: Full-guarded, surface-mounted, heavy-duty type, with general-purpose NEMA ICS 6, Type 1 enclosure.

F. Emergency Manual Operation: Equip each electrically powered door with capability for emergency manual operation. Design manual mechanism so required force for door operation does not exceed [25 lbf (111 N)] [30 lbf (133 N)] <Insert value>.

G. Emergency Operation Disconnect Device: Equip operator with hand-operated disconnect mechanism for automatically engaging manual operator and releasing brake for emergency manual operation while disconnecting motor without affecting timing of limit switch. Mount mechanism so it is accessible from floor level. Include interlock device to automatically prevent motor from operating when emergency operator is engaged.

H. Motor Removal: Design operator so motor may be removed without disturbing limit-switch adjustment and without affecting emergency manual operation.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install coiling counter doors and operating equipment complete with necessary hardware, anchors, inserts, hangers, and equipment supports; according to manufacturer's written instructions and as specified.

B. Fire-Rated Doors: Install according to NFPA 80.

C. Smoke-Control Doors: Install according to NFPA 80 and NFPA 105.

Retain option in paragraph below if weathertight installation or smoke-control doors are required.

D. Adjust hardware and moving parts to function smoothly so that doors operate easily, free of warp, twist, or distortion. Lubricate bearings and sliding parts as recommended by manufacturer.[ Adjust seals to provide tight fit around entire perimeter.]

3.2 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain coiling counter doors.

END OF SECTION 083313

	COILING COUNTER DOORS
	083313 - 1



