Copyright 2011 AIA
MasterSpec Professional
11/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 083326 - OVERHEAD COILING GRILLES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes open-curtain overhead coiling grilles.

B. Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 055000 "Metal Fabrications" for miscellaneous steel supports, angle-framing of grille opening, corner guards, and bollards.

1.2 ACTION SUBMITTALS

A. Product Data: For each type and size of overhead coiling grille and accessory.

B. Shop Drawings: For each installation and for special components not dimensioned or detailed in manufacturer's product data.

1. Include points of attachment and their corresponding static and dynamic loads imposed on structure.

2. Show locations of controls, locking devices, and other accessories.

3. Include diagrams for power, signal, and control wiring.

C. Samples: For each exposed product and for each color and texture specified.

1.3 CLOSEOUT SUBMITTALS

A. Maintenance data.

1.4 QUALITY ASSURANCE

A. Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer for both installation and maintenance of units required for this Project.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below if required for Project. Nonstructural architectural components in Seismic Design Category A are exempt from seismic design requirements; and in Seismic Design Category B, nonstructural architectural components are generally exempt. Coordinate requirements with Project's structural engineer.

A. Seismic Performance: Overhead coiling grilles shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

2.2 OPEN-CURTAIN GRILLE ASSEMBLY <Insert drawing designation>

Copy this article and re-edit for each open-curtain coiling-grille unit. This article is intended as a guide if Project requires several units of varying sizes, characteristics, and capacities. For each grille assembly, retain required options in this article and their related requirements in other Part 2 articles.

Insert drawing designation. Use these designations on Drawings to identify each product.

A. Open-Curtain Grille: Overhead coiling[, countertop] grille with a curtain having a network of horizontal rods that interconnect with vertical links.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ACME Rolling Doors.

b. Alpine Overhead Doors, Inc.

c. AlumaTek, Inc.

d. City-Gates.

e. Cookson Company.

f. Cornell Iron Works, Inc.

g. Dynamic Closures Corp.

h. Lawrence Roll-Up Doors, Inc.

i. Mahon Door Corporation.

j. McKeon Rolling Steel Door Company, Inc.

k. Metro Door.

l. Overhead Door Corporation.

m. Raynor.

n. <Insert manufacturer's name>.

Retain one option in "Operation Cycles" Paragraph below. First option is standard with some manufacturers; second option is more commonly used. Last three options are for high-cycle operation, corrosive environments, and severe or abusive use.

B. Operation Cycles: Grille components and operators capable of operating for not less than [10,000] [20,000] [50,000] [100,000] [200,000] <Insert number>.

C. Grille Curtain Material: [Aluminum] [Stainless steel] [Galvanized steel].

Retain one spacing option in "Rod Spacing" and "Link Spacing" subparagraphs below or revise to suit Project. Spacings vary among manufacturers.

1. Rod Spacing: Approximately [1-1/2 inches (38 mm)] [2 inches (51 mm)] [3 inches (76 mm)] <Insert dimension> o.c.

Three link spacings and two patterns in "Link Spacing" Subparagraph below are most commonly available; revise to suit Project.

2. Link Spacing: Approximately [3 inches (76 mm)] [6 inches (152 mm)] [9 inches (228 mm)] <Insert dimension> apart in a [straight in-line] [brick (staggered)] <Insert pattern> pattern.

Spacers between links are most often made of metal tubes; some manufacturers offer PVC spacers.

3. Spacers: [Metal tubes matching curtain material] [PVC] <Insert description>.

Retain "Bottom Bar" Paragraph below if other than manufacturer's standard bottom bar, finished to match grille, is required; revise to suit Project.

D. Bottom Bar: Continuous [tubular shape] [channel] [or] [doubled angles], fabricated from [aluminum extrusion] [hot-dip galvanized steel] [or] [stainless steel] and finished [to match grille] <Insert requirement>.

Retain last option in "Curtain Jamb Guides" Paragraph below for removable post and guides separating multiple grille installations that require a clear opening.

E. Curtain Jamb Guides: [Aluminum] [Stainless steel] [Galvanized steel] with exposed finish [matching curtain slats] <Insert requirement>. Provide continuous integral wear strips to prevent metal-to-metal contact and to minimize operational noise.[ Provide removable post(s) and jamb guides where indicated on Drawings.]

F. Hood: [Match curtain material and finish] [Aluminum] [Stainless steel] [Galvanized steel].

1. Mounting: [Face of wall] [Between jambs] [As indicated on Drawings].

Retain one of first two options in "Locking Devices" Paragraph below. Retain last option for chain-hoist-operated grilles or emergency chain-hoist operation.

G. Locking Devices: Equip grille with [slide bolt for padlock] [locking device assembly] [and] [chain lock keeper].

Retain "Locking Device Assembly" Subparagraph below if retaining second option in "Locking Devices" Paragraph above.

1. Locking Device Assembly: [Single-jamb side] [Cremone type, both jamb sides] locking bars, operable from [inside with thumb turn] [outside with cylinder] [outside only, with cylinder] [inside and outside with cylinders] <Insert requirement>.

Retain "Manual Grille Operator" or "Electric Grille Operator" Paragraph below.

H. Manual Grille Operator: [Push-up operation] [Chain-hoist operator] [Manufacturer's standard crank operator] [Awning-crank operator] [Wall-crank operator].

Retain first subparagraph below for chain or crank operator if located on other side of wall from grille curtain.

1. Provide operator with through-wall shaft operation.

Retain subparagraph below for crank operator if required.

2. Provide operator with manufacturer's standard removable operating arm.

I. Electric Grille Operator:

Retain one option in "Usage Classification" Subparagraph below or revise to suit Project. Usage classification varies among manufacturers and for each operator design; it is a durability requirement separate from whole-grille operation cycles. Consult manufacturer for specific recommendations.

1. Usage Classification: [Heavy duty, 25 or more cycles per hour and more than 90 cycles per day] [Standard duty, up to 25 cycles per hour and up to 90 cycles per day] [Medium duty, up to 12 cycles per hour and up to 50 cycles per day] [Light duty, up to 10 cycles per hour] <Insert classification>.

Retain "Safety" Subparagraph below if grille is used as an automatic garage "door." The IBC requires listing for "automatic garage door openers."

2. Safety: Listed according to UL 325 by a qualified testing agency for commercial or industrial use.

Retain one of two options in "Motor Exposure" Subparagraph below or revise to suit Project.

3. Motor Exposure: [Interior] [Exterior, wet, and humid].

4. Emergency Manual Operation: [Push-up] [Chain] [Crank] type.

Retain "Obstruction-Detection Device" Subparagraph below if grille is used as an automatic garage "door."

5. Obstruction-Detection Device: Automatic [photoelectric sensor] [electric sensor edge on bottom bar] [pneumatic sensor edge on bottom bar] [; self-monitoring] <Insert type>.

6. Control Station: [Interior mounted] [Exterior mounted] [Where indicated on Drawings] <Insert location>.

7. Other Equipment: [Audible and visual signals] [Emergency-egress release] [Self-opening mechanism] <Insert device>.

J. Curtain Accessories: Equip grille with [astragal] [push/pull handles] [and] [poll hook] <Insert item>.

K. Grille Finish:

Retain one of first four subparagraphs below. These include advertised materials and finishes; available materials and finishes vary with each manufacturer.

Second option in "Aluminum Finish" Subparagraph below is standard.

1. Aluminum Finish: [Mill] [Clear anodized] [Light bronze anodized] [Medium bronze anodized] [Dark bronze anodized] [Black anodized] [Anodized color matching Architect's sample] [Anodized color as selected by Architect from full range of industry colors and color densities] <Insert color>.

2. Baked-Enamel or Powder-Coat Finish: [Color as indicated by manufacturer's designations] [Color matching Architect's sample] [Color as selected by Architect from manufacturer's full range] <Insert color and gloss>.

3. Factory Prime Finish: Manufacturer's standard color.

Second option in "Stainless-Steel Finish" Subparagraph below is standard.

4. Stainless-Steel Finish: [No. 2B (bright, cold rolled)] [No. 4 (polished directional satin)] <Insert finish>.

Retain "PVC Spacers" Subparagraph below if required.

5. PVC Spacers: [Color as indicated by manufacturer's designations] [Color as selected by Architect from manufacturer's full range] <Insert color>.

2.3 MATERIALS, GENERAL

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.4 GRILLE CURTAIN MATERIALS AND CONSTRUCTION

A. Open-Curtain Grilles: Fabricate metal grille curtain as an open network of horizontal rods, spaced at regular intervals, that are interconnected with vertical links, which are formed and spaced as indicated and are free to rotate on the rods.

B. Bottom Bar: Manufacturer's standard continuous shape unless otherwise indicated, finished to match grille.

1. Astragal: Equip grille bottom bar with a replaceable, adjustable, continuous, compressible gasket of flexible vinyl, rubber, or neoprene as a cushion bumper.

2. Provide motor-operated grilles with combination bottom astragal and sensor edge.

C. Grille Curtain Jamb Guides: Manufacturer's standard shape having curtain groove with return lips or bars to retain curtain. Provide continuous integral wear strips to prevent metal-to-metal contact and to minimize operational noise; with removable stops on guides to prevent overtravel of curtain.

Retain subparagraph below for removable post and guides separating multiple grille installations that require a clear opening.

1. Removable Posts and Jamb Guides: Manufacturer's standard.

2.5 HOODS AND ACCESSORIES

Retain "General" Paragraph below if coiled curtain and operating mechanism are exposed (not concealed in ceiling or soffit); consider retaining a hood even if coiled grille is above ceiling.

A. General: Form sheet metal hood to entirely enclose coiled curtain and operating mechanism at opening head. Contour to fit end brackets to which hood is attached. Roll and reinforce top and bottom edges for stiffness. Form closed ends for surface-mounted hoods and fascia for any portion of between-jamb mounting that projects beyond wall face. Equip hood with intermediate support brackets as required to prevent sagging.

B. Removable Metal Soffit: Formed or extruded from same metal and with same finish as curtain if hood is mounted above ceiling, unless otherwise indicated.

C. Push/Pull Handles: Equip push-up-operated or emergency-operated grille with lifting handles on each side of grille, finished to match grille.

Retain "Pull-Down Strap" or "Pole Hooks" Paragraph below if required. Consult manufacturer for recommendations.

D. Pull-Down Strap: Provide pull-down straps for grilles more than 84 inches (2130 mm) high.

E. Pole Hooks: Provide pole hooks and poles for grilles more than 84 inches (2130 mm) high.

2.6 LOCKING DEVICES

Retain one of or both "Slide Bolt" and "Locking Device Assembly" paragraphs below for required locking device(s); revise to suit Project. First paragraph is standard for push-up grilles; revise if no padlock is required or if manufacturer's standard is a bolt on one side. Second paragraph describes a locking device with choice of locations and operation as retained in grille assembly articles in Part 2.

A. Slide Bolt: Fabricate with side-locking bolts to engage through slots in tracks for locking by padlock, located on both left and right jamb sides, operable from coil side.

B. Locking Device Assembly: Fabricate with cylinder lock, spring-loaded dead bolt, operating handle, cam plate, and adjustable locking bars to engage through slots in tracks.

Retain one of first three options in "Lock Cylinders" Subparagraph below.

1. Lock Cylinders: Cylinders [specified in Section 087100 "Door Hardware"] [specified in Section 087111 "Door Hardware (Descriptive Specification)"] [standard with manufacturer] [and keyed to building keying system].

Retain "Keys" Subparagraph below if cylinders are provided by grille manufacturer.

2. Keys: [Two] [Three] <Insert number> for each cylinder.

Retain "Chain Lock Keeper" Paragraph below for chain-hoist-operated grilles or emergency chain-hoist operation.

C. Chain Lock Keeper: Suitable for padlock.

D. Safety Interlock Switch: Equip power-operated grilles with safety interlock switch to disengage power supply when grille is locked.

2.7 COUNTERBALANCING MECHANISM

A. General: Counterbalance grilles by means of manufacturer's standard mechanism with an adjustable-tension, steel helical torsion spring mounted around a steel shaft and contained in a spring barrel connected to top of curtain with barrel rings. Use grease-sealed bearings or self-lubricating graphite bearings for rotating members.

B. Brackets: Manufacturer's standard mounting brackets of either cast iron or cold-rolled steel plate.

2.8 MANUAL GRILLE OPERATORS

Retain this article for manually operated grilles, not including electric grille operators' emergency manual operation.

A. General: Equip grille with manual grille operator by grille manufacturer.

B. Push-up Grille Operation: Lift handles and pull rope for raising and lowering grille, with counterbalance mechanism designed so that required lift or pull for grille operation does not exceed [25 lbf (111 N)] <Insert value>.

C. Chain-Hoist Operator: Consisting of endless steel hand chain, chain-pocket wheel and guard, and gear-reduction unit with a maximum [25 lbf (111 N)] [30 lbf (133 N)] <Insert value> force for grille operation. Provide alloy-steel hand chain with chain holder secured to operator guide.

"Awning" and "box" are the two types of crank operators. Indicate required type in grille assembly articles retained in Part 2.

D. Crank Operator: Consisting of crank and crank gearbox, steel crank drive shaft, and gear-reduction unit, of type indicated. Size gears to require not more than [25 lbf (111 N)] [30 lbf (133 N)] <Insert value> force to turn crank. Fabricate gearbox to be oil tight and to completely enclose operating mechanism. Provide manufacturer's standard crank-locking device.

2.9 ELECTRIC GRILLE OPERATORS

Retain this article for electric grille operators, including emergency manual operation, and for larger units or frequently operated grilles. Coordinate with Project's electrical engineer for interface of electric grille operators and equipment with fire-protection system.

A. General: Electric grille operator assembly of size and capacity recommended and provided by grille manufacturer for grille and operation cycles requirement specified, with electric motor and factory-prewired motor controls, starter, gear-reduction unit, solenoid-operated brake, clutch, control stations, control devices, integral gearing for locking grille, and accessories required for proper operation.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Chamberlain Group, Inc. (The).

b. <Insert manufacturer's name>.

3. Comply with NFPA 70.

4. Control equipment complying with NEMA ICS 1, NEMA ICS 2, and NEMA ICS 6, with NFPA 70 Class 2 control circuit, maximum 24-V ac or dc.

Durability requirement in "Usage Classification" Paragraph below is separate from "operation cycles," which apply to the whole grille system.

B. Usage Classification: Electric operator and components capable of operating for not less than number of cycles per hour indicated for each grille.

Retain option in "Motors" Paragraph below unless external controller (disconnect switch) is indicated on Drawings. Coordinate with Project's electrical engineer.

C. Motors: Reversible-type motor[ with controller (disconnect switch)] for motor exposure indicated.

1. Electrical Characteristics:

Retain one of two options in "Phase" Subparagraph below based on required motor size. Verify motor performance and availability with grille manufacturer and coordinate electrical characteristics with Project's electrical engineer. See Evaluations in Section 083323 "Overhead Coiling Doors."

a. Phase: [Single phase] [Polyphase].

b. Volts: [115] [208] [230] [460] <Insert value> V.

c. Hertz: 60.

Speed in "Motor Size" Subparagraph below is for standard-speed grilles.

2. Motor Size: Minimum size as indicated. If not indicated, large enough to start, accelerate, and operate grille in either direction from any position, at a speed not less than 8 in./sec. (203 mm/s) and not more than 12 in./sec. (305 mm/s), without exceeding nameplate ratings or service factor.

Revise "Operating Controls, Controllers (Disconnect Switches), Wiring Devices, and Wiring" Subparagraph below if required; coordinate requirements with Project's electrical engineer.

3. Operating Controls, Controllers (Disconnect Switches), Wiring Devices, and Wiring: Manufacturer's standard unless otherwise indicated.

Retain "Obstruction-Detection Device" Paragraph below if required or revise to suit Project and according to requirements of authorities having jurisdiction.

D. Obstruction-Detection Device: External entrapment protection consisting of indicated automatic safety sensor capable of protecting full width of grille opening. Activation of sensor immediately stops and reverses downward grille travel.

Retain one of or both "Photoelectric Sensor" and "Electric Sensor Edge" subparagraphs below to suit Project.

1. Photoelectric Sensor: Manufacturer's standard system designed to detect an obstruction in grille opening without contact between grille and obstruction.

Retain "Self-Monitoring Type" Subparagraph below if required.

a. Self-Monitoring Type: Designed to interface with grille operator control circuit to detect damage to or disconnection of sensing device. When self-monitoring feature is activated, grille closes only with sustained or constant pressure on close button.

2. Electric Sensor Edge: Automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar. Contact with sensor activates device. Connect to control circuit using manufacturer's standard take-up reel or self-coiling cable.

Retain "Self-Monitoring Type" Subparagraph below if required.

a. Self-Monitoring Type: Four-wire configured device designed to interface with grille operator control circuit to detect damage to or disconnection of sensor edge.

Device in "Pneumatic Sensor Edge" Subparagraph below may be limited to a width of 18 feet (5.5 m); verify availability with manufacturer.

3. Pneumatic Sensor Edge: Automatic safety sensor edge, located within astragal mounted to bottom bar. Contact with sensor activates device.

Retain "Control Station" Paragraph below for control stations in fixed locations. A sustained- or constant-pressure (in lieu of a momentary-contact) switch is required for closing according to UL 325 for commercial gates and may also be required for opening cycles according to authorities having jurisdiction; revise requirements and gate assembly articles retained in Part 2 as needed.

E. Control Station: Three-button control station in fixed location with momentary-contact push-button controls labeled "Open" and "Stop" and sustained- or constant-pressure push-button control labeled "Close."

1. Interior-Mounted Units: Full-guarded, surface-mounted, heavy-duty type, with general-purpose NEMA ICS 6, Type 1 enclosure.

2. Exterior-Mounted Units: Full-guarded, standard-duty, surface-mounted, weatherproof type; NEMA ICS 6, Type 4 enclosure, key operated.

F. Emergency Manual Operation: Equip electrically powered grille with capability for emergency manual operation. Design manual mechanism so required force for grille operation does not exceed [25 lbf (111 N)] [30 lbf (133 N)] <Insert value>.

G. Emergency Operation Disconnect Device: Equip operator with hand-operated disconnect mechanism for automatically engaging manual operator and releasing brake for emergency manual operation while disconnecting motor without affecting timing of limit switch. Mount mechanism so it is accessible from floor level. Include interlock device to automatically prevent motor from operating when emergency operator is engaged.

H. Motor Removal: Design operator so motor may be removed without disturbing limit-switch adjustment and without affecting emergency manual operation.

Remaining paragraphs are examples only; retain or revise to suit Project.

I. Audible and Visual Signals: Audible alarm and visual indicator lights in compliance with regulatory requirements for accessibility.

Retain one of or both "Emergency-Egress Release" and "Self-Opening Mechanism" paragraphs below if required. Verify requirements with authorities having jurisdiction.

J. Emergency-Egress Release: Flush, wall-mounted handle mechanism, for accessibility-code-compliant egress feature, not dependent on electric power. The release allows an unlocked grille to partially open without affecting limit switches to permit passage, and it automatically resets motor drive upon return of handle to original position.

K. Self-Opening Mechanism: Automatic release mechanism triggered by [smoke detector,] [emergency push-button station,] fire alarm or power failure. When activated, the grille self-opens by means of a fail-safe operator to the fully open position without the need for power operation or battery backup systems. When the[ emergency push-button is reset, and the] alarm is cleared and power is restored, the grille will operate normally.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install overhead coiling grilles and operating equipment complete with necessary hardware, anchors, inserts, hangers, and equipment supports, according to manufacturer's written instructions and as specified.

Option in "Power-Operated Grilles" Paragraph below is according to minimum IBC requirement for "automatic garage door openers." Delete option to include all power-operated grilles.

B. Power-Operated Grilles: Install[ automatic garage grille openers] according to UL 325.

C. Adjust hardware and moving parts to function smoothly, so that grilles operate easily, free of warp, twist, or distortion. Lubricate bearings and sliding parts as recommended by manufacturer.

3.2 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain overhead coiling grilles.

END OF SECTION 083326
	OVERHEAD COILING GRILLES
	083326 - 1



