Copyright 2012 AIA
MasterSpec Professional
05/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 104416 - FIRE EXTINGUISHERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes portable, hand-carried fire extinguishers[ and mounting brackets for fire extinguishers].

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1.3 INFORMATIONAL SUBMITTALS

A. Warranty: Sample of special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 COORDINATION

Consider retaining this article if fire-protection cabinets are specified by series only or for complex projects.

A. Coordinate type and capacity of fire extinguishers with fire-protection cabinets to ensure fit and function.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for fire extinguishers with manufacturers.

1. Warranty Period: [Six] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

A. NFPA Compliance: Fabricate and label fire extinguishers to comply with NFPA 10, "Portable Fire Extinguishers."

B. Fire Extinguishers: Listed and labeled for type, rating, and classification by an independent testing agency acceptable to authorities having jurisdiction.

2.2 PORTABLE, HAND-CARRIED FIRE EXTINGUISHERS

See the tables at the end of the Evaluations for a list of manufacturers' products. Use these tables in combination with manufacturers' catalogs or product data to insert series, type, model, and designations of other characteristics.

A. Fire Extinguishers: Type, size, and capacity for each [fire-protection cabinet] [and] [mounting bracket] indicated.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Amerex Corporation.

b. Ansul Incorporated.

c. Badger Fire Protection.

d. Buckeye Fire Equipment Company.

e. Fire End & Croker Corporation.

f. Guardian Fire Equipment, Inc.

g. JL Industries, Inc.; a division of the Activar Construction Products Group.

h. Kidde Residential and Commercial Division; Subsidiary of Kidde plc.

i. Larsens Manufacturing Company.

j. Moon American.

k. Nystrom Building Products.

l. Pem All Fire Extinguisher Corp.

m. Potter Roemer LLC.

n. Pyro-Chem; Tyco Safety Products.

o. Strike First Corporation of America.

p. <Insert manufacturer's name>.

3. Instruction Labels: Include pictorial marking system complying with NFPA 10, Appendix B[, and bar coding for documenting fire-extinguisher location, inspections, maintenance, and recharging].

In remaining paragraphs, the letter A, B, or C indicates the class of fire on which an extinguisher is effective. Class A and Class B are preceded by a rating numeral indicating the extinguisher's relative extinguishing effectiveness. Extinguishers for Class C fires are not required to have a rating numeral. See the Evaluations for fire classifications and numerical rating explanation.

In retained paragraphs below, insert drawing designation. Use these designations on Drawings to identify each product.

Retain one or more of first three paragraphs below for stored-pressure water-type extinguishers. Potential for freezing exists with all types. Retain second paragraph if freeze potential is high.

B. Stored-Pressure Water Type <Insert drawing designation>: UL-rated 2-A, 2.5-gal. (9.5-L) nominal capacity, with water in stainless-steel container; with pressure-indicating gage.

C. Stored-Pressure Antifreeze Water Type <Insert drawing designation>: UL-rated 2-A, 2.5-gal. (9.5-L) nominal capacity, with water and approved antifreeze solution mixed for temperatures as low as minus 40 deg F (minus 40 deg C) in stainless-steel container; with pressure-indicating gage.

D. Stored-Pressure Water-Mist Type <Insert drawing designation>: UL-rated 2-A:C, 2.5-gal. (9.5-L) nominal capacity, with water in enameled-steel container; with pressure-indicating gage.

E. Regular Dry-Chemical Type <Insert drawing designation>: UL-rated <Insert capacity> nominal capacity, with sodium bicarbonate-based dry chemical in manufacturer's standard enameled container.

F. Multipurpose Dry-Chemical Type <Insert drawing designation>: UL-rated <Insert capacity> nominal capacity, with monoammonium phosphate-based dry chemical in manufacturer's standard enameled container.

G. Carbon Dioxide Type <Insert drawing designation>: UL-rated [5-B:C, 5-lb (2.3-kg)] [10-B:C, 10-lb (4.5-kg)] [10-B:C, 15-lb (6.8-kg)] [10-B:C, 20-lb (9.1-kg)] nominal capacity, with carbon dioxide in manufacturer's standard enameled-metal container.

"Clean-Agent Type in Steel Container" Paragraph below describes Ansul's fire extinguishers using FE-36 clean agent as an alternative to halon. See the Evaluations.

H. Clean-Agent Type in Steel Container <Insert drawing designation>: UL-rated [5-B:C, 4.75-lb (2.2-kg)] [1-A:10-B:C, 10-lb (4.5-kg)] [2-A:10-B:C, 14-lb (6.4-kg)] nominal capacity, with HFC blend agent and inert material in enameled-steel container; with pressure-indicating gage.

Insert other types and capacities to suit Project.

2.3 MOUNTING BRACKETS <Insert drawing designation>

Retain this article if mounting brackets separate from fire-protection cabinets are required.

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

A. Mounting Brackets: Manufacturer's standard[ galvanized] steel, designed to secure fire extinguisher to wall or structure, of sizes required for types and capacities of fire extinguishers indicated, with plated or [red] [black] baked-enamel finish.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Amerex Corporation.

b. Ansul Incorporated.

c. Badger Fire Protection.

d. Buckeye Fire Equipment Company.

e. Fire End & Croker Corporation.

f. Guardian Fire Equipment, Inc.

g. JL Industries, Inc.; a division of the Activar Construction Products Group.

h. Larsens Manufacturing Company.

i. Nystrom Building Products.

j. Potter Roemer LLC.

k. Strike First Corporation of America.

l. <Insert manufacturer's name>.

B. Identification: Lettering complying with authorities having jurisdiction for letter style, size, spacing, and location. Locate as indicated by Architect.

1. Identify bracket-mounted fire extinguishers with the words "FIRE EXTINGUISHER" in red letter decals applied to mounting surface.

If more than one orientation is required, indicate location of each on Drawings.

a. Orientation: [Vertical] [Horizontal].

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Examine fire extinguishers for proper charging and tagging.

1. Remove and replace damaged, defective, or undercharged fire extinguishers.

B. Install fire extinguishers[ and mounting brackets] in locations indicated and in compliance with requirements of authorities having jurisdiction.

According to NFPA 10, maximum mounting height for fire extinguishers weighing 40 lb (18 kg) or less is 60 inches (1524 mm); for those weighing more, it is 42 inches (1067 mm).

1. Mounting Brackets: [54 inches (1372 mm)] <Insert dimension> above finished floor to top of fire extinguisher.

C. Mounting Brackets: Fasten mounting brackets to surfaces, square and plumb, at locations indicated.

END OF SECTION 104416

	FIRE EXTINGUISHERS
	104416 - 1



