Copyright 2010 AIA
MasterSpec Professional
05/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 144119 - STAIRWAY CHAIRLIFTS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

Categories in paragraph below are covered by ASME A18.1. Stairway chairlifts are not permitted for accessible routes under the U.S. Architectural & Transportation Barriers Compliance Board's ADA-ABA Accessibility Guidelines and under ICC A117.1.

A. Section includes [inclined] [private-residence, inclined] stairway chairlifts.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For each lift.

1. Include plans, elevations, sections, details, attachments to other work, and required clearances.

2. Indicate dimensions, weights, loads, and points of load to building structure.

3. Include diagrams for power, signal, and control wiring.

C. Samples: For each exposed product and for each color and texture specified.

1.3 INFORMATIONAL SUBMITTALS

A. Product certificates.

B. Sample warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

B. Inspection and acceptance certificates and operating permits.

1.5 QUALITY ASSURANCE

A. Installer Qualifications: An authorized representative who is trained and approved by manufacturer.

1.6 WARRANTY

A. Special Warranty: Manufacturer agrees to repair or replace components of lifts that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for lifts and components.

1. Warranty Period: [Two] [Four] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

A. Regulatory Requirements: Comply with ASME A18.1, "Safety Standard for Platform Lifts and Stairway Chairlifts."

2.2 INCLINED STAIRWAY CHAIRLIFT <Insert drawing designation>

Inclined stairway chairlifts are not permitted for accessible routes under ADA-ABA Accessibility Guidelines and ICC A117.1.

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

A. [Private-Residence, ]Inclined Stairway Chairlift, General: Preengineered lift system.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Bruno Independent Living Aids, Inc.
b. Savaria Concord Lifts.
c. ThyssenKrupp Access.
d. <Insert manufacturer's name>.

B. Rated Capacity: Minimum [250 lb (115 kg)] <Insert value>.

Verify available speeds with manufacturers.

C. Rated Speed: [18 fpm (0.09 m/s)] [20 fpm (0.10 m/s)] [22 fpm (0.11 m/s)] [25 fpm (0.13 m/s)] <Insert value>.

D. Power Supply: 120 V, 60 Hz, one phase.

Retain one of or both "Battery Operation" and "Manual Lowering" paragraphs below; verify availability of these features with manufacturers.

E. Battery Operation: Provide battery-operated drive with automatic charging system.

F. Manual Lowering: Provide means to manually lower units in case of malfunction or power loss.

G. Folding Units: When not in use, units shall be capable of manually folding up against wall to minimize projection into stairway.

H. Support to Structure: Provide brackets to support vertical loads from floor or stair treads and to support lateral loads from walls. Fabricate brackets from steel plates, shapes, or bars.

I. Accessories: Provide units with the following accessories:

Retain any of or all three subparagraphs below; verify availability with manufacturers.

1. Tubular-steel, manually operated safety arms designed to restrain and provide grab bar for occupant.

2. Retractable seatbelt.

Subparagraph below is required by ASME A18.1 except for private-residence units.

3. Seat with back and two handgrips or arms.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Wiring Method: Conceal conductors and cables within housings of units or building construction.

B. Adjust stops for accurate stopping at each landing.

C. Lubricate operating parts of lift, including drive mechanism, guide rails, hinges, safety devices, and hardware.

D. Test safety devices and verify smoothness of required protective enclosures and other surfaces.

3.2 FIELD QUALITY CONTROL

A. Acceptance Testing: On completion of lift installation and before permitting use of lifts, perform acceptance tests as required and recommended by ASME A18.1 and authorities having jurisdiction.

B. Operating Test: In addition to acceptance testing, load lifts to rated capacity and operate continuously for 30 minutes between lowest and highest landings served. Readjust stops, signal equipment, and other devices for accurate stopping and operation of system.

3.3 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain lifts. Include a review of emergency systems and emergency procedures to be followed at time of operational failure and other building emergencies.

B. Check operation of lifts with Owner's personnel present and before date of Substantial Completion. Determine that operating systems and devices are functioning properly.

C. Check operation of lifts with Owner's personnel present not more than one month before end of warranty period. Determine that operating systems and devices are functioning properly.

END OF SECTION 144119

	STAIRWAY CHAIRLIFTS
	144119 - 1



