Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 210523 - GENERAL-DUTY VALVES FOR WATER-BASED FIRE-SUPPRESSION PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Iron butterfly valves with indicators.

2. Check valves.

3. Iron OS&Y gate valves.

4. NRS gate valves.

5. Indicator posts.

6. Trim and drain valves.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of valve.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 GENERAL REQUIREMENTS FOR VALVES

Retain "UL Listed" or "FM Global Approved" Paragraph below, or both, depending on requirements of authorities having jurisdiction at Project location. Unless stated otherwise, all manufacturers listed in the product types below supply valves that are both UL listed and FM Global approved. See "Codes" Article in the Evaluations for more information.

Consult authorities having jurisdiction for Project to verify acceptable valve materials and other products. Fire codes have different requirements for acceptable valve materials.

A. UL Listed: Valves shall be listed in UL's "Online Certifications Directory" under the headings listed below and shall bear UL mark:

1. Main Level: HAMV - Fire Main Equipment.

a. Level 1: HCBZ - Indicator Posts, Gate Valve.

b. Level 1: HLOT - Valves.

1) Level 3: HLUG - Ball Valves, System Control.

2) Level 3: HLXS - Butterfly Valves.

3) Level 3: HMER - Check Valves.

4) Level 3: HMRZ - Gate Valves.

2. Main Level: VDGT - Sprinkler System & Water Spray System Devices.

a. Level 1: VQGU - Valves, Trim and Drain.

B. FM Global Approved: Valves shall be listed in its "Approval Guide," under the headings listed below:

1. Automated Sprinkler Systems:

a. Indicator posts.

b. Valves.

1) Gate valves.

2) Check valves.

a) Single check valves.

3) Miscellaneous valves.

C. Source Limitations for Valves: Obtain valves for each valve type from single manufacturer.

D. ASME Compliance:

1. ASME B16.1 for flanges on iron valves.

2. ASME B1.20.1 for threads for threaded-end valves.

3. ASME B31.9 for building services piping valves.

E. AWWA Compliance: Comply with AWWA C606 for grooved-end connections.

F. NFPA Compliance: Comply with NFPA 24 for valves.

Caution: Fire-protection valves have a minimum pressure rating of 175 psig (1030 kPa), which drops to 150 psig (1200 kPa) for valves larger than NPS 12 (DN 300). Revise pressure ratings in valve articles if valves with higher ratings are required. Verify pressure requirements for large valves. Coordinate minimum pressure ratings with Drawings and system-pressure requirements.

G. Valve Pressure Ratings: Not less than the minimum pressure rating indicated or higher as required by system pressures.

H. Valve Sizes: Same as upstream piping unless otherwise indicated.

I. Valve Actuator Types:

1. Worm-gear actuator with handwheel for quarter-turn valves, except for trim and drain valves.

2. Handwheel: For other than quarter-turn trim and drain valves.

3. Handlever: For quarter-turn trim and drain valves NPS 2 (DN 50) and smaller.

2.2 IRON BUTTERFLY VALVES WITH INDICATORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Anvil International, Inc.

2. Fivalco Inc.

3. Globe Fire Sprinkler Corporation.

4. Kennedy Valve; a division of McWane, Inc.

5. NIBCO INC.

6. Tyco Fire & Building Products LP.

7. Victaulic Company.

8. <Insert manufacturer's name>.

C. Description:

Revising subparagraphs below require updating the list of manufacturers above. No manufacturer supplies every option listed below.

1. Standard: UL 1091 and FM Global standard for indicating valves, (butterfly or ball type), Class Number 112.

2. Minimum Pressure Rating: 175 psig (1200 kPa).

3. Body Material: Cast or ductile iron[ with nylon, EPDM, epoxy, or polyamide coating].

4. Seat Material: EPDM.

5. Stem: Stainless steel.

6. Disc: Ductile iron, [nickel plated] [and EPDM or SBR coated].

7. Actuator: Worm gear or traveling nut.

Retain "Supervisory Switch" Subparagraph below only if switch is not specified elsewhere.

8. Supervisory Switch: Internal or external.

9. Body Design: [Lug or wafer] [Grooved-end connections].

Valves specified in "Check Valves" Article below are available in NPS 2 (DN 50) and larger.

2.3 CHECK VALVES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Anvil International, Inc.

2. Fire Protection Products, Inc.

3. Fivalco Inc.

4. Globe Fire Sprinkler Corporation.

5. Kennedy Valve; a division of McWane, Inc.

6. Matco-Norca.

7. Mueller Co.; Water Products Division.

8. NIBCO INC.

9. Reliable Automatic Sprinkler Co., Inc.

10. Shurjoint Piping Products.

11. Tyco Fire & Building Products LP.

12. United Brass Works, Inc.

13. Venus Fire Protection Ltd.

14. Victaulic Company.

15. Viking Corporation.

16. Watts Water Technologies, Inc.

17. Wilson & Cousins Inc.

18. <Insert manufacturer's name>.

C. Description:

Revising subparagraphs below requires updating the list of manufacturers above.

1. Standard: UL 312 and FM Global standard for swing check valves, Class Number 1210.

2. Minimum Pressure Rating: 175 psiga (1200 kPa).

3. Type: Single swing check.

4. Body Material: Cast iron, ductile iron, or bronze.

5. Clapper: Bronze, ductile iron, or stainless steel[ with elastomeric seal].

6. Clapper Seat: Brass, bronze, or stainless steel.

7. Hinge Shaft: Bronze or stainless steel.

8. Hinge Spring: Stainless steel.

9. End Connections: Flanged, grooved, or threaded.

2.4 IRON OS&Y GATE VALVES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Cast Iron Pipe Company; Waterous Company subsidiary.

2. Clow Valve Company; a division of McWane, Inc.

3. Hammond Valve.

4. Kennedy Valve; a division of McWane, Inc.

5. Mueller Co.; Water Products Division.

6. NIBCO INC.

7. Victaulic Company.

8. Watts Water Technologies, Inc.

9. <Insert manufacturer's name>.

C. Description:

Revising subparagraphs below requires updating the list of manufacturers above. No manufacturer supplies every option listed below.

1. Standard: UL 262 and FM Global standard for fire-service water control valves (OS&Y- and NRS-type gate valves).

2. Minimum Pressure Rating: 175 psig (1200 kPa).

3. Body and Bonnet Material: Cast or ductile iron.

4. Wedge: Cast or ductile iron, or bronze[ with elastomeric coating].

5. Wedge Seat: Cast or ductile iron, or bronze[ with elastomeric coating].

6. Stem: Brass or bronze.

7. Packing: Non-asbestos PTFE.

Retain "Supervisory Switch" Subparagraph below only if switch is not specified elsewhere.

8. Supervisory Switch: External.

9. End Connections: [Flanged] [Grooved] [Threaded].

Valves in "NRS Gate Valves" Article below are available in NPS 2 (DN 50) and larger.

2.5 NRS GATE VALVES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Cast Iron Pipe Company; Waterous Company subsidiary.

2. Clow Valve Company; a division of McWane, Inc.

3. Kennedy Valve; a division of McWane, Inc.

4. Mueller Co.; Water Products Division.

5. NIBCO INC.

6. Victaulic Company.

7. <Insert manufacturer's name>.

C. Description:

Revising subparagraphs below requires updating the list of manufacturers above.

1. Standard: UL 262 and FM Global standard for fire-service water control valves (OS&Y- and NRS-type gate valves).

2. Minimum Pressure Rating: 175 psig (1200 kPa).

3. Body and Bonnet Material: Cast or ductile iron.

4. Wedge: Cast or ductile iron[ with elastomeric coating].

5. Wedge Seat: Cast or ductile iron, or bronze[ with elastomeric coating].

6. Stem: Brass or bronze.

7. Packing: Non-asbestos PTFE.

Retain "Supervisory Switch" Subparagraph below only if switch is not specified elsewhere.

8. Supervisory Switch: External.

9. End Connections: [Flanged] [Grooved] [Threaded].

Retain "Indicator Posts" Article below with "NRS Gate Valves" Article above. Indicator posts below are available in NPS 3 (DN 75) and larger.

2.6 INDICATOR POSTS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Cast Iron Pipe Company; Waterous Company subsidiary.

2. Clow Valve Company; a division of McWane, Inc.

3. Kennedy Valve; a division of McWane, Inc.

4. Mueller Co.; Water Products Division.

5. NIBCO INC.

6. <Insert manufacturer's name>.

C. Description:

1. Standard: UL 789 and FM Global standard for indicator posts.

2. Type: [Underground] [Pit] [Wall].

3. Base Barrel Material: [Cast or ductile iron] [PVC].

Retain "Extension Barrel" Subparagraph below if the indicator post is adjustable in length. Below is not applicable to wall-type post indicators.

4. Extension Barrel: Cast or ductile iron.

5. Cap: Cast or ductile iron.

6. Operation: [Wrench] [Handwheel].

2.7 TRIM AND DRAIN VALVES

Trim and drain valves are UL listed and are NPS 2 (DN 50) and smaller. No UL standard exists for these valves. Some valves used for trim and drain systems may be approved by FM Global, but no specific FM Global trim and drain category exists where these valves are located. See Evaluations for more information.

A. Angle Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Fire Protection Products, Inc.

b. NIBCO INC.

c. United Brass Works, Inc.

d. <Insert manufacturer's name>.

3. Description:

a. Pressure Rating: [175 psig (1200 kPa)] [250 psig (1720 kPa)] [300 psig (2070 kPa)].

b. Body Material: Brass or bronze.

c. Ends: Threaded.

d. Stem: Bronze.

e. Disc: Bronze.

f. Packing: Asbestos free.

g. Handwheel: Malleable iron, bronze, or aluminum.

PART 3 -  EXECUTION

3.1 GENERAL REQUIREMENTS FOR VALVE INSTALLATION

A. Comply with requirements in the following Sections for specific valve installation requirements and applications:

1. Section 211100 "Facility Fire-Suppression Water-Service Piping" for application of valves in fire-suppression water-service piping outside the building.

2. Section 211200 "Fire-Suppression Standpipes" for application of valves in fire-suppression standpipes.

3. Section 211313 "Wet-Pipe Sprinkler Systems" for application of valves in wet-pipe, fire-suppression sprinkler systems.

4. Section 211316 "Dry-Pipe Sprinkler Systems" for application of valves in dry-pipe, fire-suppression sprinkler systems.

5. Section 211339 "Foam-Water Systems" for application of valves in AFFF piping.

B. Install listed fire-protection shutoff valves supervised-open, located to control sources of water supply except from fire-department connections. Install permanent identification signs indicating portion of system controlled by each valve.

C. Install check valve in each water-supply connection. Install backflow preventers instead of check valves in potable-water-supply sources.

D. Install valves having threaded connections with unions at each piece of equipment arranged to allow easy access, service, maintenance, and equipment removal without system shutdown. Provide separate support where necessary.

E. Install valves in horizontal piping with stem at or above the pipe center.

F. Install valves in position to allow full stem movement.

G. Install valve tags. Comply with requirements in Section 210553 "Identification for Fire-Suppression Piping and Equipment" for valve tags and schedules and signs on surfaces concealing valves; and the NFPA standard applying to the piping system in which valves are installed. Install permanent identification signs indicating the portion of system controlled by each valve.

H. Install listed fire-protection shutoff valves supervised-open, located to control sources of water supply except from fire-department connections.

I. Install check valve in each water-supply connection. Install backflow preventers instead of check valves in potable-water-supply sources.

END OF SECTION 210523

	GENERAL-DUTY VALVES FOR WATER-BASED FIRE-SUPPRESSION PIPING
	210523 - 1



