Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 210533 - HEAT TRACING FOR FIRE-SUPPRESSION PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes heat tracing for fire-suppression piping with the following electric heating cables:

1. Plastic insulated, series resistance.

2. Self-regulating, parallel resistance.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 220533 "Heat Tracing for Plumbing Piping."

2. Section 230533 "Heat Tracing for HVAC Piping."

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For electric heating cable.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

B. Sample Warranty: For special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for electric heating cable. Special warranties often exclude labor.

1. Warranty Period: [Three] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PLASTIC-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Delta-Therm Corporation.

2. Easy Heat; a division of EGS Electrical Group LLC.

3. Pyrotenax; a brand of Tyco Thermal Controls LLC.

4. Raychem; a brand of Tyco Thermal Controls LLC.

5. Watts Radiant, Inc.; a subsidiary of Watts Water Technologies, Inc.

6. <Insert manufacturer's name>.

C. Comply with IEEE 515.1.

D. Heating Element: Single- or dual-stranded resistor wire. Terminate with waterproof, factory-assembled nonheating leads with connectors at both ends.

E. Electrical Insulating Jacket: Minimum 4.0-mil (0.10-mm) Kapton with silicone, Tefzel, or polyolefin.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover: Aluminum braid[ and silicone or Hylar outer jacket or TPR overjacket].

G. Maximum Operating Temperature (Power On): [150 deg F (65 deg C)] <Insert temperature>.

Verify temperature of circulated media in freeze-protected piping in "Maximum Exposure Temperature (Power Off)" Paragraph below.

H. Maximum Exposure Temperature (Power Off): [185 deg F (85 deg C)] <Insert temperature>.

I. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70 and NFPA 13, by a qualified testing agency, and marked for intended location and application.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for a sample schedule.

J. Capacities and Characteristics:

1. Maximum Heat Output: [6 W/ft. (19.7 W/m)] [7.5 W/ft. (24.6 W/m)] <Insert value>.

2. Piping Diameter: <Insert NPS (DN)>.

3. Number of Parallel Cables: <Insert number>.

4. Spiral Wrap Pitch: <Insert inches (mm)>.

5. Electrical Characteristics for Single-Circuit Connection:

Verify available voltages and heat-output ratings with manufacturer.

a. Volts: [120] [208] [240] [277] [480] <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.2 SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. BriskHeat.

2. Chromalox.

3. Delta-Therm Corporation.

4. Easy Heat; a division of EGS Electrical Group LLC.

5. Nelson Heat Trace; a division of EGS Electrical Group LLC.

6. Pyrotenax; a brand of Tyco Thermal Controls LLC.

7. Raychem; a brand of Tyco Thermal Controls LLC.

8. Thermon Americas Inc.

9. Trasor Corp.

10. <Insert manufacturer's name>.

C. Comply with IEEE 515.1.

D. Heating Element: Pair of parallel [No. 16] [No. 18] AWG, [tinned] [nickel-coated], stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length. Terminate with waterproof, factory-assembled, nonheating leads with connectors at one end, and seal the opposite end watertight. Cable shall be capable of crossing over itself once without overheating.

E. Electrical Insulating Jacket: Flame-retardant polyolefin.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover: [Tinned-copper] [Stainless-steel] braid[ and polyolefin outer jacket with ultraviolet inhibitor].

G. Maximum Operating Temperature (Power On): [150 deg F (65 deg C)] <Insert temperature>.

Verify temperature of circulated media in freeze-protected piping in "Maximum Exposure Temperature (Power Off)" Paragraph below.

H. Maximum Exposure Temperature (Power Off): [185 deg F (85 deg C)] <Insert temperature>.

I. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for a sample schedule.

J. Capacities and Characteristics:

1. Maximum Heat Output: [3 W/ft. (9.8 W/m)] [5 W/ft. (16.4 W/m)] [8 W/ft. (26 W/m)] [10 W/ft. (32.8 W/m)] [12 W/ft. (39.4 W/m)] <Insert value>.

2. Piping Diameter: <Insert NPS (DN)>.

3. Number of Parallel Cables: <Insert number>.

4. Spiral Wrap Pitch: <Insert inches (mm)>.

5. Electrical Characteristics for Single-Circuit Connection:

Verify available voltages and heat-output ratings with manufacturer.

a. Volts: [120] [208] [240] [277] [480] <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.3 CONTROLS

A. Remote bulb unit with adjustable temperature range from [30 to 50 deg F (minus 1 to plus 10 deg C)] <Insert temperature range>.

B. Snap action; open-on-rise, single-pole switch with minimum current rating adequate for connected cable.

C. Remote bulb on capillary, resistance temperature device, or thermistor for directly sensing pipe-wall temperature.

D. Corrosion-resistant, waterproof control enclosure.

2.4 ACCESSORIES

A. Cable Installation Accessories: Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer or as recommended in writing by manufacturer.

B. Warning Tape: Continuously printed "Electrical Tracing"; vinyl, at least 3 mils (0.08 mm) thick, and with pressure-sensitive, permanent, waterproof, self-adhesive back.

1. Width for Markers on Pipes with OD, Including Insulation, Less Than 6 Inches (150 mm): 3/4 inch (19 mm) minimum.

2. Width for Markers on Pipes with OD, Including Insulation, 6 Inches (150 mm) or Larger: 1-1/2 inches (38 mm) minimum.

PART 3 -  EXECUTION

3.1 INSTALLATION

Indicate location of controls on Drawings.

Most manufacturers of heat-tracing cable for fire suppression recommend that the cables be installed on standpipe and sprinkler piping main lines, between buildings, on piping in unheated areas, or on piping through coolers or freezers. Manufacturers recommend against using the heat-tracing cables on branch lines as protection against freezing of branch lines and sprinklers.

A. Install electric heating cable where indicated and according to NFPA 70 and NFPA 13.

B. Install electric heating cables after piping has been tested and before insulation is installed.

C. Install electric heating cables according to IEEE 515.1.

D. Install insulation over piping with electric cables according to Section 210700 "Fire-Suppression Systems Insulation."

E. Install warning tape on piping insulation where piping is equipped with electric heating cables.

F. Set field-adjustable switches and circuit-breaker trip ranges.

G. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

H. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

Indication location of controls on Drawings. According to NFPA 13, heat tracing must be monitored by a fire-alarm system. Coordinate with requirements in (Section 283111 "Digital, Addressable Fire-Alarm System.")(Section 283112 "Zoned (DC Loop) Fire-Alarm System.")

I. Connect heat-tracing controls to fire-alarm system according to NFPA 13. Comply with requirements in [Section 283111 "Digital, Addressable Fire-Alarm System."] [Section 283112 "Zoned (DC Loop) Fire-Alarm System."]

3.2 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform tests after cable installation but before application of coverings such as insulation, wall or ceiling construction, or concrete.

2. Test cables for electrical continuity and insulation integrity before energizing.

3. Test cables to verify rating and power input. Energize and measure voltage and current simultaneously.

B. Repeat tests for continuity, insulation resistance, and input power after applying thermal insulation on pipe-mounted cables.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Cables will be considered defective if they do not pass tests and inspections.

D. Prepare test and inspection reports.

E. Remove and replace damaged heat-tracing cables.

END OF SECTION 210533

	HEAT TRACING FOR FIRE-SUPPRESSION PIPING
	210533 - 1



