Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 211100 - FACILITY FIRE-SUPPRESSION WATER-SERVICE PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes fire-suppression water-service piping and related components outside the building [and service entrance piping through floor into the building] [and service entrance piping through wall into the building] and the following:

1. Pipes, fittings, and specialties.

2. Fire-suppression specialty valves.

3. Concrete vaults.

4. Protective enclosures.

5. Alarm devices.

Utility companies usually provide water meters and bill charges directly or through Contractor to Owner. Contact utility company serving the site for information. Delete first paragraph below if water meters are provided by utility company or Contractor. If utility company furnishes water meters, identify the company here, specify what it does, and revise text to suit Project.

B. Utility-furnished products include water meters that are furnished to the site, ready for installation.

C. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 211116 "Facility Fire Hydrants" for AWWA and UL-listed, dry- and wet-barrel fire hydrants.

2. Section 211119 "Fire-Department Connections" for exposed-, flush-, and yard-type, fire-department connections.

3. Section 211200 "Fire-Suppression Standpipes" for fire-suppression standpipes inside the building.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings:

1. Detail precast concrete vault assemblies and indicate dimensions, method of field assembly, and components.

Retain subparagraph below if equipment includes wiring.

2. Include diagrams for power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: For piping and specialties including relation to other services in same area, drawn to scale. Show piping and specialty sizes and valves, meter and specialty locations, and elevations.

B. Field quality-control reports.

1.4 QUALITY ASSURANCE

Retain and revise "Regulatory Requirements" Paragraph below to suit Project, or delete if not applicable.

A. Regulatory Requirements:

1. Comply with requirements of utility company supplying the water. Include tapping of water mains and backflow prevention.

2. Comply with standards of authorities having jurisdiction for fire-suppression water-service piping, including materials, hose threads, installation, and testing.

B. Piping materials shall bear label, stamp, or other markings of specified testing agency.

C. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Comply with FM Global's "Approval Guide" or UL's "Fire Protection Equipment Directory" for fire-service-main products.

E. NFPA Compliance: Comply with NFPA 24 for materials, installations, tests, flushing, and valve and hydrant supervision for fire-suppression water-service piping.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

First five articles below include examples of materials used for water-distribution piping. See "Writing Guide" Article in the Evaluations.

2.1 COPPER TUBE AND FITTINGS

Tube in "Soft Copper Tube" Paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

A. Soft Copper Tube: [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)], water tube, annealed temper.

Tube in "Hard Copper Tube" Paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

B. Hard Copper Tube: [ASTM B 88, Type K (ASTM B 88M, Type A)] [and] [ASTM B 88, Type L (ASTM B 88M, Type B)], water tube, drawn temper.

C. Copper, Solder-Joint Fittings: ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint pressure type. Furnish only wrought-copper fittings if indicated.

D. Copper, Pressure-Seal Fittings:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Viega; Plumbing & Heating Systems.

b. <Insert manufacturer's name>.

2. Standard: UL 213.

3. NPS 2 (DN 50) and Smaller: Wrought-copper fitting with EPDM O-ring seal in each end.

4. NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Bronze fitting with stainless-steel grip ring and EPDM O-ring seal in each end.

Flanges in "Bronze Flanges" Paragraph below are available in NPS 1/2 to NPS 12 (DN 15 to DN 300).

E. Bronze Flanges: ASME B16.24, Class 150, with solder-joint end. Furnish Class 300 flanges if required to match piping.

Unions in "Copper Unions" Paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100). NFPA 13 limits unions to NPS 2 (DN 50) and smaller.

F. Copper Unions: MSS SP-123, cast-copper-alloy, hexagonal-stock body with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

2.2 DUCTILE-IRON PIPE AND FITTINGS

Ductile-iron pipe is intended for fire-suppression water-service-piping outside the building and underslab within the building.

Pipe in "Grooved-Joint, Ductile-Iron Pipe" Paragraph below is available in NPS 3 to NPS 24 (DN 80 to DN 600).

A. Grooved-Joint, Ductile-Iron Pipe: AWWA C151, with cut, rounded-grooved ends.

Pipe in "Mechanical-Joint, Ductile-Iron Pipe" Paragraph below is available in NPS 3 to NPS 24 (DN 80 to DN 600).

B. Mechanical-Joint, Ductile-Iron Pipe: AWWA C151, with mechanical-joint bell and plain spigot end.

Pipe in "Push-on-Joint, Ductile-Iron Pipe" Paragraph below is available in NPS 3 to NPS 48 (DN 80 to DN 1200).

C. Push-on-Joint, Ductile-Iron Pipe: AWWA C151, with push-on-joint bell and plain spigot end.

D. Grooved-End, Ductile-Iron Pipe Appurtenances:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Corcoran Piping Systems Inc.

c. Shurjoint Piping Products.

d. Star Pipe Products.

e. Tyco Fire & Building Products LP.

f. Venus Fire Protection Ltd.

g. Victaulic Company.

h. Viking Corporation.

i. <Insert manufacturer's name>.

Fittings and couplings in "Grooved-End, Ductile-Iron Fittings" and "Grooved-End, Ductile-Iron-Piping Couplings" subparagraphs below are available in NPS 3 to NPS 24 (DN 80 to DN 600).

2. Grooved-End, Ductile-Iron Fittings: ASTM A 47/A 47M, malleable-iron castings or ASTM A 536, ductile-iron castings with dimensions matching pipe.

3. Grooved-End, Ductile-Iron-Piping Couplings: AWWA C606, for ductile-iron-pipe dimensions. Include ferrous housing sections, gasket suitable for water, and bolts and nuts.

E. Mechanical-Joint, Ductile-Iron Fittings: AWWA C110, ductile- or gray-iron standard pattern or AWWA C153, ductile-iron compact pattern.

1. Glands, Gaskets, and Bolts: AWWA C111, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

Fittings in "Push-on-Joint, Ductile-Iron Fittings" Paragraph below are available in NPS 3 to NPS 48 (DN 80 to DN 1200).

F. Push-on-Joint, Ductile-Iron Fittings: AWWA C153, ductile-iron compact pattern.

1. Gaskets: AWWA C111, rubber.

Flanges in "Flanges" Paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

G. Flanges: ASME B16.1, Class 125, cast iron.

2.3 PE PIPE AND FITTINGS

Pipe in "PE, Fire-Service Pipe" Paragraph below is FM Global approved in NPS 2 to NPS 12 (DN 50 to DN 300).

A. PE, Fire-Service Pipe: FM Global approved, with minimum thickness equivalent to [Class 150] [and] [Class 200].

B. Molded PE Fittings: FM Global approved; PE butt-fusion type, made to match PE pipe dimensions and class.

2.4 PVC PIPE AND FITTINGS

Pipe in "PVC Pipe" Paragraph below is UL listed in NPS 4 to NPS 12 (DN 100 to DN 300).

A. PVC Pipe: [AWWA C900] [or] [UL 1285], [Class 150] [and] [Class 200], with bell end with gasket, and with spigot end.

B. PVC Fittings: [AWWA C900] [or] [UL 1285], [Class 150] [and] [Class 200], with bell-and-spigot or double-bell ends. Include elastomeric gasket in each bell.

2.5 SPECIAL PIPE FITTINGS

A. Ductile-Iron Flexible Expansion Joints:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. EBAA Iron, Inc.

b. ROMAC Industries Inc.

c. Star Pipe Products.

d. <Insert manufacturer's name>.

2. Description: Compound, ductile-iron fitting with combination of flanged and mechanical-joint ends complying with AWWA C110 or AWWA C153. Include two gasketed ball-joint sections and one or more gasketed sleeve sections. Assemble components for offset and expansion indicated. Include AWWA C111, ductile-iron glands, rubber gaskets, and steel bolts.

3. Pressure Rating: 250 psig (1725 kPa) minimum.

B. Ductile-Iron Deflection Fittings:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. EBAA Iron, Inc.

b. <Insert manufacturer's name>.

2. Description: Compound, ductile-iron coupling fitting with sleeve and one or two flexing sections for up to 15-degree deflection, gaskets, and restrained-joint ends complying with AWWA C110 or AWWA C153. Include AWWA C111, ductile-iron glands, rubber gaskets, and steel bolts.

3. Pressure Rating: 250 psig (1725 kPa) minimum.

2.6 JOINING MATERIALS

A. Gaskets for Ferrous Piping and Copper-Alloy Tubing: ASME B16.21, asbestos free.

B. Brazing Filler Metals: AWS A5.8/A5.8M, BCuP Series.

2.7 PIPING SPECIALTIES

A. Transition Fittings: Manufactured fitting or coupling same size as, with pressure rating at least equal to and ends compatible with, piping to be joined.

B. Tubular-Sleeve Pipe Couplings:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cascade Waterworks Manufacturing.

b. Dresser, Inc.; Dresser Piping Specialties.

c. Ford Meter Box Company, Inc. (The); Pipe Products Division.

d. JCM Industries.

e. ROMAC Industries Inc.

f. Smith-Blair, Inc.; a Sensus company.

g. Viking Johnson.

h. <Insert manufacturer's name>.

2. Description: Metal, bolted, sleeve-type, reducing or transition coupling, with center sleeve, gaskets, end rings, and bolt fasteners, and with ends of same sizes as piping to be joined.

3. Standard: AWWA C219.

4. Center-Sleeve Material: [Manufacturer's standard] [Carbon steel] [Stainless steel] [Ductile iron] [Malleable iron].

5. Gasket Material: Natural or synthetic rubber.

6. Pressure Rating: [150 psig (1035 kPa)] [200 psig (1380 kPa)] <Insert value> minimum.

7. Metal Component Finish: Corrosion-resistant coating or material.

2.8 CORPORATION VALVES

Caution: High-pressure valves in this article are rated for 150 psig (1035 kPa), but most manufacturers' valves have a higher pressure rating.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Ford Meter Box Company, Inc. (The); Pipe Products Division.

2. Jones, James Company.

3. Master Meter, Inc.

4. McDonald, A. Y. Mfg. Co.

5. Mueller Co.; Water Products Division.

6. Red Hed Manufacturing & Supply.

7. <Insert manufacturer's name>.

Retain "Corporation Valves" Paragraph below for tapping connections NPS 2 (DN 50) and smaller.

B. Corporation Valves: Comply with AWWA C800. Include saddle and valve compatible with tapping machine[ and manifold].

1. Service Saddle: Copper alloy with seal and AWWA C800, threaded outlet for corporation valve.

2. Corporation Valve: Bronze body and ground-key plug, with AWWA C800, threaded inlet and outlet matching service piping material.

Retain "Manifold" Subparagraph below if utility company requires multiple connections.

3. Manifold: Copper fitting with two to four inlets as required, with ends matching corporation valves and outlet matching service piping material.

C. Meter Valves: Comply with AWWA C800 for high-pressure, service-line valves. Include angle- or straight-through-pattern bronze body, ground-key plug or ball, and wide tee head, with inlet and outlet matching service piping material.

2.9 CURB VALVES

Caution: High-pressure valves in this article are rated for 150 psig (1035 kPa), but most manufacturers' valves have a higher pressure rating.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Ford Meter Box Company, Inc. (The); Pipe Products Division.

2. Jones, James Company.

3. Master Meter, Inc.

4. McDonald, A. Y. Mfg. Co.

5. Mueller Co.; Water Products Division.

6. Red Hed Manufacturing & Supply.

7. <Insert manufacturer's name>.

B. Curb Valves: Comply with AWWA C800 for high-pressure, service-line valves. Valve has bronze body, ground-key plug or ball, wide tee head, and inlet and outlet matching service piping material.

C. Service Boxes for Curb Valves: Similar to AWWA M44 requirements for cast-iron valve boxes. Include cast-iron telescoping top section of length required for depth of burial of valve, plug with lettering "WATER," and bottom section with base that fits over curb valve and with a barrel approximately 3 inches (75 mm) in diameter.

1. Shutoff Rods: Steel; with tee-handle with one pointed end, stem of length to operate deepest buried valve, and slotted end matching curb valve.

D. Meter Valves: Comply with AWWA C800 for high-pressure, service-line valves. Include angle- or straight-through-pattern bronze body, ground-key plug or ball, and wide tee head, with inlet and outlet matching service piping material.

2.10 DETECTOR CHECK VALVES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

2. Badger Meter, Inc.

3. FEBCO; SPX Valves & Controls.

4. Flomatic Corporation.

5. Mueller Co.; Hersey Meters Division.

6. Watts Water Technologies, Inc.

7. <Insert manufacturer's name>.

C. Description: Galvanized cast-iron body, bolted cover with air-bleed device for access to internal parts, and flanged ends. Include one-piece bronze disc with bronze bushings, pivot, and replaceable seat. Include threaded bypass taps in inlet and outlet for bypass meter connection. Set valve to allow minimal water flow through bypass meter when major water flow is required.

D. Standards: UL 312 and FM Global's "Approval Guide."

E. Pressure Rating: 175 psig (1200 kPa).

F. Water Meter: AWWA C700, disc type, at least one-fourth size of detector check valve. Include meter, bypass piping, gate valves, check valve, and connections to detector check valve.

2.11 WATER METERS

A. Water meters are furnished by utility company.

If utility company furnishes water meters, identify utility company in "Summary" Article and delete remaining paragraphs in this article. If water meters are specified in this Section, delete paragraph above, retain remaining paragraphs below, and revise to suit Project.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

B. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. AMCO Water Metering Systems.

2. Badger Meter, Inc.

3. Carlon Meter.

4. Hays Fluid Controls.

5. McCrometer.

6. Mueller Co.; Hersey Meters Division.

7. Neptune Technology Group Inc.

8. Sensus Metering Systems.

9. <Insert manufacturer's name>.

Retain "Displacement-Type Water Meters," "Turbine-Type Water Meters," or "Compound-Type Water Meters" Paragraph below. Verify, with utility company and authorities having jurisdiction, type of meter required.

C. Displacement-Type Water Meters:

1. Description: With bronze main case.

2. Standard: AWWA C700.

3. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

D. Turbine-Type Water Meters:

1. Standard: AWWA C701.

2. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

E. Compound-Type Water Meters:

1. Standard: AWWA C702.

2. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

Retain one of two "Remote Registration System" paragraphs below if required; revise to suit Project.

F. Remote Registration System:

1. Description: Utility company's standard; direct-reading type. Include meter modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly.

2. Standard: AWWA C706.

3. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

G. Remote Registration System:

1. Description: Utility company's standard; encoder type. Include meter modified with signal-transmitting assembly, low-voltage connecting wiring, and remote register assembly.

2. Standard: AWWA C707.

3. Registration: Flow in [gallons (liters)] [cubic feet (cubic meters)].

Retain "Data-Acquisition Units" or "Visible Display Units" Subparagraph below; revise to suit Project.

4. Data-Acquisition Units: Comply with utility company's requirements for type and quantity.

5. Visible Display Units: Comply with utility company's requirements for type and quantity.

2.12 PRESSURE-REDUCING VALVES

Copy "Water Regulators" Paragraph below and re-edit for each type of water regulator required.

Water regulators in paragraph are available in NPS 1/2 to NPS 3 (DN 15 to DN 80).

A. Water Regulators:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Cash Acme; a division of The Reliance Worldwide Corporation.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Honeywell Water Controls.

d. Watts Water Technologies, Inc.

e. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

f. <Insert manufacturer's name>.

3. Standard: ASSE 1003.

4. Pressure Rating: Initial pressure of 150 psig (1035 kPa).

5. Size: <Insert NPS (DN)>.

6. Design Flow Rate: <Insert gpm (L/s)>.

7. Design Inlet Pressure: <Insert psig (kPa)>.

8. Design Outlet Pressure Setting: <Insert psig (kPa)>.

9. Body Material: Bronze[ with chrome-plated finish] for NPS 2 (DN 50) and smaller; cast iron[ with interior lining complying with AWWA C550 or that is FDA approved] for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

10. End Connections: Threaded for NPS 2 (DN 50) and smaller; flanged for NPS 2-1/2 and NPS 3 (DN 65 and DN 80).

Copy "Water Control Valves" Paragraph below and re-edit for each type of water control valve required.

Water control valves in paragraph are available in NPS 1-1/4 (DN 32) and larger.

B. Water Control Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. CLA-VAL Automatic Control Valves.

b. Flomatic Corporation.

c. Globe Fire Sprinkler Corporation.

d. OCV Control Valves.

e. Reliable Automatic Sprinkler Co., Inc.

f. Tyco Fire & Building Products LP.

g. Victaulic Company.

h. Viking Corporation.

i. Watts Regulator Company; Ames Fluid Control Systems.

j. Watts Regulator Company; Watts ACV Division.

k. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

l. <Insert manufacturer's name>.

3. Description: Pilot-operation, diaphragm-type, single-seated main water control valve with AWWA C550 or FDA-approved, interior epoxy coating. Include small pilot control valve, restrictor device, specialty fittings, and sensor piping.

4. Pressure Rating: Initial pressure of 150 psig (1035 kPa) minimum.

5. Main Valve Body: Cast or ductile iron with AWWA C550 or FDA-approved, interior epoxy coating; or stainless-steel body.

a. Size: <Insert NPS (DN)>.

b. Pattern: [Angle] [Globe]-valve design.

c. Trim: Stainless steel.

6. Design Flow Rate: <Insert gpm (L/s)>.

7. Design Inlet Pressure: <Insert psig (kPa)>.

8. Design Outlet Pressure Setting: <Insert psig (kPa)>.

9. End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

2.13 BACKFLOW PREVENTERS

Verify, with authorities having jurisdiction, whether AWWA, or UL-listed, or FM Global-approved backflow preventers are required.

Copy "Double-Check, Backflow-Prevention Assemblies" Paragraph below and re-edit for each type of double-check, backflow-prevention assembly required.

Double-check, backflow-prevention assemblies in paragraph are for low hazard and are available in NPS 3/4 to NPS 10 (DN 20 to DN 250).

A. Double-Check, Backflow-Prevention Assemblies:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Mueller Co.; Water Products Division.

f. Watts Water Technologies, Inc.

g. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

h. <Insert manufacturer's name>.

3. Standard: [ASSE 1015] [or] [AWWA C510].

4. Operation: Continuous-pressure applications unless otherwise indicated.

5. Pressure Loss: [5 psig (35 kPa)] <Insert value> maximum, through middle one-third of flow range.

6. Size: <Insert NPS (DN)>.

7. Design Flow Rate: <Insert gpm (L/s)>.

8. Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

9. Pressure Loss at Design Flow Rate: <Insert psig (kPa)> for NPS 2 (DN 50) and smaller; <Insert psig (kPa)> for NPS 2-1/2 (DN 65) and larger.

10. Body Material: Bronze for NPS 2 (DN 50) and smaller; [cast iron with interior lining complying with AWWA C550 or that is FDA approved] [steel with interior lining complying with AWWA C550 or that is FDA approved] [stainless steel] for NPS 2-1/2 (DN 65) and larger.

11. End Connections: Threaded for NPS 2 (DN 50) and smaller; [flanged] <Insert type> for NPS 2-1/2 (DN 65) and larger.

12. Configuration: Designed for [horizontal, straight through] <Insert configuration> flow.

13. Accessories: Ball valves with threaded ends on inlet and outlet of NPS 2 (DN 50) and smaller; OS&Y gate valves with flanged ends on inlet and outlet of NPS 2-1/2 (DN 65) and larger.

Copy "Double-Check, Detector-Assembly Backflow Preventers" Paragraph below and re-edit for each type of double-check, detector-assembly backflow preventer required.

Double-check, detector-assembly backflow preventers in paragraph are for low hazard and are available in NPS 3 to NPS 10 (DN 80 to DN 250).

B. Double-Check, Detector-Assembly Backflow Preventers:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Mueller Co.

e. Watts Water Technologies, Inc.

f. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

g. <Insert manufacturer's name>.

3. Standards: ASSE 1048 and UL's "Fire Protection Equipment Directory" listing or FM Global's "Approval Guide."

4. Operation: Continuous-pressure applications.

5. Pressure Loss: [5 psig (35 kPa)] <Insert value> maximum, through middle one-third of flow range.

6. Size: <Insert NPS (DN)>.

7. Design Flow Rate: <Insert gpm (L/s)>.

8. Selected Unit Flow Range Limits: <Insert gpm (L/s)>.

9. Pressure Loss at Design Flow Rate: <Insert psig (kPa)>.

10. Body Material: [Cast iron with interior lining complying with AWWA C550 or that is FDA approved] [Steel with interior lining complying with AWWA C550 or that is FDA approved] [Stainless steel].

11. End Connections: Flanged.

12. Configuration: Designed for [horizontal, straight through] [vertical inlet, horizontal center section, and vertical outlet] [vertical] <Insert configuration> flow.

13. Accessories:

a. Valves: UL 262 and FM Global's "Approval Guide" listing; OS&Y gate type with flanged ends on inlet and outlet.

b. Bypass: With displacement-type water meter, shutoff valves, and reduced-pressure backflow preventer.

Copy "Backflow Preventer Test Kits" Paragraph below and re-edit for each type of backflow preventer test kit required.

C. Backflow Preventer Test Kits:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Ames Fire & Waterworks; a division of Watts Water Technologies, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. FEBCO; SPX Valves & Controls.

d. Flomatic Corporation.

e. Watts Water Technologies, Inc.

f. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

g. <Insert manufacturer's name>.

2. Description: Factory calibrated, with gages, fittings, hoses, and carrying case with test-procedure instructions.

2.14 WATER METER BOXES

Retain one of three "Description" paragraphs in this article.

A. Description: Cast-iron body and cover for disc-type water meter, with lettering "WATER METER" on cover; and with slotted, open-bottom base section of length to fit over service piping.

Retain "Option" Subparagraph below if permitted.

1. Option: Base section may be cast-iron, PVC, clay, or other pipe.

B. Description: Cast-iron body and double cover for disc-type water meter, with lettering "WATER METER" on top cover; and with separate inner cover; air space between covers; and slotted, open-bottom base section of length to fit over service piping.

Use meter box in "Description" Paragraph below in walks or unpaved areas away from traffic; do not use in roadways.

C. Description: Polymer-concrete body and cover for disc-type water meter, with lettering "WATER" on cover; and with slotted, open-bottom base section of length to fit over service piping. Include vertical and lateral design loadings of 15,000 lb minimum over 10 by 10 inches (6 800 kg minimum over 254 by 254 mm) square.

2.15 CONCRETE VAULTS

Retain this article if vaults are required and are not specified in Section 033000 "Cast-in-Place Concrete" or Section 033053 "Miscellaneous Cast-in-Place Concrete."

A. Description: Precast, reinforced-concrete vault, designed for A-16 load designation according to ASTM C 857, and made according to ASTM C 858.

B. Ladder: ASTM A 36/A 36M, steel ladder; or PE-encased steel steps.

Retain one of two "Manhole" paragraphs below.

C. Manhole: ASTM A 48/A 48M, Class No. 35A minimum tensile strength, gray-iron traffic frame and cover.

1. Dimension: 24-inch (610-mm) minimum diameter unless otherwise indicated.

D. Manhole: ASTM A 536, Grade 60-40-18, ductile-iron traffic frame and cover.

1. Dimension: 24-inch (610-mm) minimum diameter unless otherwise indicated.

E. Drain: ASME A112.6.3, cast-iron floor drain with outlet of size indicated. Include body anchor flange, light-duty cast-iron grate, bottom outlet, and integral or field-installed bronze ball or clapper-type backwater valve.

2.16 ALARM DEVICES

A. General: UL 753 and FM Global's "Approval Guide" listing, of types and sizes to mate and match piping and equipment.

Devices in "Water-Flow Indicators," "Supervisory Switches," and "Pressure Switches" paragraphs below are usually located inside the building and are specified in Section 211200 "Fire-Suppression Standpipes" and Section 211313 "Wet-Pipe Sprinkler Systems." Verify requirements with authorities having jurisdiction. Indicators in first paragraph mount on pipe with vane in water and can be used with wet-barrel fire hydrants.

B. Water-Flow Indicators: Vane-type water-flow detector, rated for 250-psig (1725-kPa) working pressure; designed for horizontal or vertical installation; with two single-pole, double-throw circuit switches to provide isolated alarm and auxiliary contacts, 7 A, 125-V ac and 0.25 A, 24-V dc; complete with factory-set, field-adjustable retard element to prevent false signals and tamperproof cover that sends signal when cover is removed.

Switches in "Supervisory Switches" Paragraph below mount on stem of OS&Y gate valves and on indicator posts.

C. Supervisory Switches: Single pole, double throw; designed to signal valve in other than fully open position.

Switches in "Pressure Switches" Paragraph below mount on barrel of dry-barrel fire hydrants.

D. Pressure Switches: Single pole, double throw; designed to signal increase in pressure.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Comply with excavating, trenching, and backfilling requirements in Section 312000 "Earth Moving."

3.2 PIPING INSTALLATION

Retain one of two "Water-Main Connection" paragraphs below. Retain first paragraph if tap is made by utility company; retain second if tap is made by Contractor.

A. Water-Main Connection: Arrange with water utility company for tap of size and in location indicated in water main.

B. Water-Main Connection: Tap water main according to requirements of water utility company and of size and in location indicated.

Retain first paragraph below for tapping of pipe with connections larger than NPS 2 (DN 50).

C. Make connections larger than NPS 2 (DN 50) with tapping machine according to the following:

1. Install tapping sleeve and tapping valve according to MSS SP-60.

2. Install tapping sleeve on pipe to be tapped. Position flanged outlet for gate valve.

3. Use tapping machine compatible with valve and tapping sleeve; cut hole in main. Remove tapping machine and connect water-service piping.

4. Install gate valve onto tapping sleeve. Comply with MSS SP-60. Install valve with stem pointing up and with valve box.

Retain first paragraph below for tapping of pipe with connections NPS 2 (DN 50) and smaller.

D. Make connections NPS 2 (DN 50) and smaller with drilling machine according to the following:

1. Install service-saddle assemblies and corporation valves in size, quantity, and arrangement required by utility company's standards.

2. Install service-saddle assemblies on water-service pipe to be tapped. Position outlets for corporation valves.

3. Use drilling machine compatible with service-saddle assemblies and corporation valves. Drill hole in main. Remove drilling machine and connect water-service piping.

4. Install corporation valves into service-saddle assemblies.

5. Install manifold for multiple taps in water main.

6. Install curb valve in water-service piping with head pointing up and with service box.

E. Comply with NFPA 24 for fire-service-main piping materials and installation.

F. Install copper tube and fittings according to CDA's "Copper Tube Handbook."

G. Install ductile-iron, water-service piping according to AWWA C600 and AWWA M41.

Retain subparagraph below if required.

1. Install encasement for piping according to ASTM A 674 or AWWA C105.

H. Install PE pipe according to ASTM D 2774 and ASTM F 645.

I. Install PVC, AWWA pipe according to ASTM F 645 and AWWA M23.

Revise first paragraph below for required minimum depth if known.

J. Bury piping with depth of cover over top at least [30 inches (750 mm)] <Insert dimension>, with top at least [12 inches (300 mm)] <Insert dimension> below level of maximum frost penetration, and according to the following:

1. Under Driveways: With at least [36 inches (910 mm)] <Insert dimension> of cover over top.

2. Under Railroad Tracks: With at least [48 inches (1220 mm)] <Insert dimension> of cover over top.

3. In Loose Gravelly Soil and Rock: With at least [12 inches (300 mm)] <Insert dimension> of additional cover.

K. Install piping by tunneling or jacking, or combination of both, under streets and other obstructions that cannot be disturbed.

L. Extend fire-suppression water-service piping and connect to water-supply source and building fire-suppression water-service piping systems at locations and pipe sizes indicated.

1. Terminate fire-suppression water-service piping within the building at the [floor slab] [wall] until building-water-piping systems are installed. Terminate piping with caps, plugs, or flanges as required for piping material. Make connections to building's fire-suppression water-service piping systems when those systems are installed.

Retain first paragraph below for piping with gasketed joints and revise to suit Project; delete if not required.

M. Install underground piping with restrained joints at horizontal and vertical changes in direction. Use restrained-joint piping, thrust blocks, anchors, tie-rods and clamps, and other supports.

N. Comply with requirements in Section 211200 "Fire-Suppression Standpipes," Section 211313 "Wet-Pipe Sprinkler Systems," and Section 211316 "Dry-Pipe Sprinkler Systems" for fire-suppression-water piping inside the building.

O. Comply with requirements in Section 221116 "Domestic Water Piping" for potable-water piping inside the building.

P. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Retain paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

Q. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

3.3 JOINT CONSTRUCTION

A. Install couplings, flanges, flanged fittings, unions, nipples, and transition and special fittings that have finish and pressure rating same as or higher than systems pressure rating for aboveground applications unless otherwise indicated.

B. Install unions adjacent to each valve in tubing NPS 2 (DN 50) and smaller.

C. Install flanges, flange adaptors, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

D. Ream ends of tubes and remove burrs.

E. Remove scale, slag, dirt, and debris from outside and inside of pipes, tubes, and fittings before assembly.

F. Copper-Tubing, Brazed Joints: Join copper tube and fittings according to CDA's "Copper Tube Handbook," "Brazed Joints" Chapter.

G. Copper-Tubing, Pressure-Sealed Joints: Use proprietary crimping tool and procedure recommended by copper, pressure-seal-fitting manufacturer.

H. Ductile-Iron Piping, Gasketed Joints for Fire-Service-Main Piping: UL 194.

I. Ductile-Iron Piping, Grooved Joints: Cut-groove pipe. Assemble joints with grooved-end, ductile-iron-piping couplings, gaskets, lubricant, and bolts.

J. Flanged Joints: Select appropriate gasket material in size, type, and thickness suitable for water service. Join flanges with bolts according to ASME B31.9.

K. PE Piping Heat-Fusion Joints: Clean and dry joining surfaces by wiping with clean cloth or paper towels. Join according to ASTM D 2657.

L. PVC Piping Gasketed Joints: Use joining materials according to AWWA C900. Construct joints with elastomeric seals and lubricant according to ASTM D 2774 or ASTM D 3139.

M. Dissimilar Materials Piping Joints: Use adapters compatible with both piping materials, with OD, and with system working pressure.

N. Do not use flanges or unions for underground piping.

3.4 ANCHORAGE INSTALLATION

Delete this article if anchorages are not required.

A. Anchorage, General: Install water-distribution piping with restrained joints. Anchorages and restrained-joint types that may be used include the following:

Retain subparagraphs below for types of anchorages and restrained joints permitted.

1. Concrete thrust blocks.

2. Locking mechanical joints.

3. Set-screw mechanical retainer glands.

4. Bolted flanged joints.

5. Heat-fused joints.

6. Pipe clamps and tie rods.

7. <Insert devices>.

B. Install anchorages for tees, plugs and caps, bends, crosses, valves, and hydrant branches in fire-suppression water-service piping according to NFPA 24 and the following:

1. Gasketed-Joint, Ductile-Iron, Water-Service Piping: According to AWWA C600.

2. Gasketed-Joint, PVC Water-Service Piping: According to AWWA M23.

C. Apply full coat of asphalt or other acceptable corrosion-resistant material to surfaces of installed ferrous anchorage devices.

3.5 VALVE INSTALLATION

A. AWWA Gate Valves: Comply with AWWA C600 and AWWA M44. Install each underground valve with stem pointing up and with valve box.

B. AWWA Valves Other Than Gate Valves: Comply with AWWA C600 and AWWA M44.

C. UL-Listed or FM Global-Approved Gate Valves: Comply with NFPA 24. Install each underground valve and valves in vaults with stem pointing up and with vertical cast-iron indicator post.

D. UL-Listed or FM Global-Approved Valves Other Than Gate Valves: Comply with NFPA 24.

E. MSS Valves: Install as component of connected piping system.

F. Corporation Valves and Curb Valves: Install each underground curb valve with head pointed up and with service box.

G. Pressure-Reducing Valves: Install in vault or aboveground between shutoff valves.[ Install full-size valved bypass.]

H. Support valves and piping, not direct buried, on concrete piers. Comply with requirements for concrete piers in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

3.6 DETECTOR CHECK VALVE INSTALLATION

A. Install in vault or aboveground.

B. Install for proper direction of flow. Install bypass with water meter, gate valves on each side of meter, and check valve downstream from meter.

C. Support detector check valves and piping on concrete piers. Comply with requirements for concrete piers in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

3.7 WATER METER INSTALLATION

Delete this article if utility company provides water meters.

A. Install water meters, piping, and specialties according to utility company's written instructions.

Retain one or more of two "Water Meters" paragraphs below.

B. Water Meters: Install [displacement] [turbine]-type water meters NPS 2 (DN 50) and smaller in meter boxes with shutoff valves on water meter inlets. Include valves on water meter outlets, and include valved bypass around meters unless prohibited by authorities having jurisdiction.

C. Water Meters: Install [compound] [turbine]-type water meters NPS 3 (DN 80) and larger in meter vaults. Include shutoff valves on water meter inlets and outlets, and include valved bypass around meters. Support meters, valves, and piping on brick or concrete piers.

D. Support water meters and piping NPS 3 (DN 80) and larger on concrete piers. Comply with requirements for concrete piers in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

3.8 ROUGHING-IN FOR WATER METERS

Retain this article if Contractor is to rough-in for water meters to be installed by utility company.

A. Rough-in piping and specialties for water meter installation according to utility company's written instructions.

3.9 BACKFLOW PREVENTER INSTALLATION

A. Install backflow preventers of type, size, and capacity indicated. Include valves and test cocks. Install according to requirements of plumbing and health department and authorities having jurisdiction.

B. Do not install backflow preventers that have relief drain in vault or in other spaces subject to flooding.

C. Do not install bypass piping around backflow preventers.

Revise or delete paragraph below to suit Project.

D. Support NPS 2-1/2 (DN 65) and larger backflow preventers and piping on concrete piers. Comply with requirements for concrete piers in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

3.10 WATER METER BOX INSTALLATION

A. Install water meter boxes in paved areas flush with surface.

B. Install water meter boxes in grass or earth areas with top [2 inches (50 mm)] <Insert dimension> above surface.

3.11 CONCRETE VAULT INSTALLATION

A. Install precast concrete vaults according to ASTM C 891.

3.12 FIRE-DEPARTMENT CONNECTION INSTALLATION

A. Install ball drip valves at each check valve for fire-department connection to mains.

B. Install protective pipe bollards [on two sides of] [on three sides of] <Insert arrangement> each freestanding fire-department connection. Pipe bollards are specified in Section 055000 "Metal Fabrications."

3.13 ALARM DEVICE INSTALLATION

Delete this article if alarm devices are specified in Section 211200 "Fire-Suppression Standpipes" or Section 221313 "Wet-Pipe Sprinkler Systems."

A. General: Comply with NFPA 24 for devices and methods of valve supervision. Underground valves with valve box do not require supervision.

Retain "Supervisory Switches" or "Locking and Sealing" Paragraph below to suit requirements of authorities having jurisdiction.

B. Supervisory Switches: Supervise valves in open position.

1. Valves: Grind away portion of exposed valve stem. Bolt switch, with plunger in stem depression, to OS&Y gate-valve yoke.

2. Indicator Posts: Drill and thread hole in upper-barrel section at target plate. Install switch, with toggle against target plate, on barrel of indicator post.

C. Locking and Sealing: Secure unsupervised valves as follows:

1. Valves: Install chain and padlock on open OS&Y gate valve.

2. Post Indicators: Install padlock on wrench on indicator post.

D. Pressure Switches: Drill and thread hole in exposed barrel of fire hydrant. Install switch.

E. Water-Flow Indicators: Install in water-service piping in vault. Select indicator with saddle and vane matching pipe size. Drill hole in pipe, insert vane, and bolt saddle to pipe.

F. Connect alarm devices to building's fire-alarm system. Wiring and fire-alarm devices are specified in [Section 283111 "Digital, Addressable Fire-Alarm System."] [Section 283112 "Zoned (DC Loop) Fire-Alarm System."]

3.14 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect fire-suppression water-service piping to [utility water main] [existing water main] <Insert piping system>. Use [tapping sleeve and tapping valve] [service clamp and corporation valve] <Insert method>.

B. Connect fire-suppression water-service piping to interior fire-suppression piping.

C. Connect waste piping from concrete vault drains to [sanitary sewerage system. Comply with requirements in Section 221313 "Facility Sanitary Sewers" for connection to sanitary sewer] [storm-drainage system. Comply with requirements in Section 334100 "Storm Utility Drainage Piping" for connection to storm sewer].

3.15 FIELD QUALITY CONTROL

Revise this article to suit requirements of authorities having jurisdiction.

A. Use test procedure prescribed by authorities having jurisdiction or, if method is not prescribed by authorities having jurisdiction, use procedure described below.

B. Piping Tests: Conduct piping tests before joints are covered and after concrete thrust blocks have hardened sufficiently. Fill pipeline 24 hours before testing and apply test pressure to stabilize system. Use only potable water.

C. Hydrostatic Tests: Test at not less than one-and-one-half times the working pressure for two hours.

1. Increase pressure in 50-psig (350-kPa) increments and inspect each joint between increments. Hold at test pressure for one hour; decrease to zero psig (zero kPa). Slowly increase again to test pressure and hold for one more hour. Maximum allowable leakage is 2 quarts (1.89 L) per hour per 100 joints. Remake leaking joints with new materials and repeat test until leakage is within allowed limits.

D. Prepare test and inspection reports.

3.16 IDENTIFICATION

A. Install continuous underground[ detectable] warning tape during backfilling of trench for underground fire-suppression water-service piping. Locate below finished grade, directly over piping. Underground warning tapes are specified in Section 312000 "Earth Moving."

Retain paragraph below if using nonmetallic fire-suppression water-service piping or fire-suppression water-service piping with electrically insulated fittings.

B. Permanently attach equipment nameplate or marker indicating plastic fire-suppression water-service piping or fire-suppression water-service piping with electrically insulated fittings, on main electrical meter panel. Comply with requirements for identifying devices in Section 220553 "Identification for Plumbing Piping and Equipment."

3.17 PIPING SCHEDULE

See Editing Instruction No. 2 in the Evaluations for cautions about selecting products.

Retain one or more piping applications in this article. Coordinate with materials specified in Part 2.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Underground fire-suppression water-service piping [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be[ one of] the following:

Retain subparagraph below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. NPS 2 (DN 50) PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Underground fire-suppression water-service piping NPS 3 (DN 80) shall be[ one of] the following:

Retain one or more of four subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and gasketed joints.

4. PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

C. Underground fire-suppression water-service piping NPS 4 (DN 100) shall be[ one of] the following:

Retain one or more of five subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and gasketed joints.

4. PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

5. PVC, [Class 150] [Class 200] pipe listed for fire-protection service; PVC fittings of same class as pipe; and gasketed joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

D. Underground fire-suppression water-service piping [NPS 6 to NPS 12 (DN 150 to DN 300)] <Insert pipe size range> shall be[ one of] the following:

Retain one or more of five subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and gasketed joints.

4. PE, [Class 150] [Class 200], fire-service pipe; molded PE fittings; and heat-fusion joints.

5. PVC, [Class 150] [Class 200] pipe listed for fire-protection service; PVC fittings of same class as pipe; and gasketed joints.

E. [Aboveground] [and] [vault] fire-suppression water-service piping [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be hard copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought- or cast-copper-alloy, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

F. [Aboveground] [and] [vault] fire-suppression water-service piping [NPS 3 and NPS 4 (DN 80 and DN 100)] <Insert pipe size range> shall be[ one of] the following:

Retain subparagraph below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

G. [Aboveground] [and] [vault] fire-suppression water-service piping [NPS 5 to NPS 12 (DN 125 to DN 300)] <Insert pipe size range> shall be grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

Piping in three paragraphs below is for fire-suppression water-service piping that is installed, buried in earth, below the lowest floor, and within the building footprint; retain if required.

H. Underslab fire-suppression water-service piping [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be soft copper tube, [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)]; [wrought-copper, solder-joint fittings; and brazed] [copper, pressure-seal fittings; and pressure-sealed] joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

I. Underslab fire-suppression water-service piping [NPS 3 and NPS 4 (DN 80 and DN 100)] <Insert pipe size range> shall be[ one of] the following:

Retain one or more of three subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and restrained, gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and restrained, gasketed joints.

Retain " one of" option in paragraph below to allow Contractor to select piping materials from those retained.

J. Underslab fire-suppression water-service piping [NPS 6 to NPS 12 (DN 150 to DN 300)] <Insert pipe size range> shall be[ one of] the following:

Retain one or more of three subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. Grooved-end, ductile-iron pipe; grooved-end, ductile-iron pipe appurtenances; and grooved joints.

2. Mechanical-joint, ductile-iron pipe; mechanical-joint, [ductile- or gray-iron, standard-pattern] [or] [ductile-iron, compact-pattern] fittings; glands, gaskets, and bolts; and restrained, gasketed joints.

3. Push-on-joint, ductile-iron pipe; push-on-joint, ductile-iron compact-pattern fittings; and restrained, gasketed joints.

3.18 VALVE SCHEDULE

See Editing Instruction No. 2 in the Evaluations for cautions about selecting products.

Retain one or more valve applications in this article. Coordinate with materials specified in Part 2.

A. Underground fire-suppression water-service shutoff valves NPS 2 (DN 50) and smaller shall be corporation valves or curb valves with ends compatible with piping.

B. Meter box fire-suppression water-service shutoff valves NPS 2 (DN 50) and smaller shall be meter valves.

C. Vault fire-suppression water-service shutoff valves NPS 2 (DN 50) and smaller shall be [Class 125, MSS, bronze, nonrising stem] [or] [UL-listed or FM Global-approved, OS&Y, bronze,] gate valves.

Retain " one of" option in first paragraph below to allow Contractor to select valve materials from those retained.

D. Underground fire-suppression water-service shutoff valves NPS 3 (DN 80) and larger shall be[ one of] the following:

Retain one or more of three subparagraphs below. If using more than one type of valve, identify various valve types on Drawings.

1. 200-psig (1380-kPa), AWWA, iron, nonrising-stem, [metal] [resilient]-seated gate valves.

2. 250-psig (1725-kPa), AWWA, iron, nonrising-stem, resilient-seated gate valves.

3. [175-psig (1200-kPa)] [250-psig (1725-kPa)], UL-listed or FM Global-approved, iron, nonrising-stem gate valves.

E. Indicator-post underground fire-suppression water-service valves NPS 3 (DN 80) and larger shall be [175-psig (1200-kPa)] [250-psig (1725-kPa)], UL-listed or FM Global-approved, iron, nonrising-stem gate valves with indicator-post flange.

Retain " one of" option in first paragraph below to allow Contractor to select valve materials from those retained.

F. Standard-pressure, [aboveground] [and] [vault] fire-suppression water-service shutoff valves NPS 3 (DN 80) and larger shall be[ one of] the following:

Retain one or more of four subparagraphs below. If using more than one type of valve, identify various valve types on Drawings.

1. 200-psig (1380-kPa), AWWA, iron, OS&Y, [metal] [resilient]-seated gate valves.

2. 250-psig (1725-kPa), AWWA, iron, OS&Y, resilient-seated gate valves.

3. [175-psig (1200-kPa)] [250-psig (1725-kPa)], UL-listed or FM Global-approved, iron, OS&Y gate valves.

4. [AWWA] [or] [UL-listed or FM Global-approved] butterfly valves.

Retain " one of" option in paragraph below to allow Contractor to select valve materials from those retained.

G. Fire-suppression water-service check valves NPS 3 (DN 80) and larger shall be[ one of] the following:

Retain one or both subparagraphs below. If using more than one type of valve, identify various valve types on Drawings.

1. [AWWA] [or] [UL-listed or FM Global-approved] check valves.

2. UL-listed or FM Global-approved detector check valves.

END OF SECTION 211100

	FACILITY FIRE-SUPPRESSION WATER-SERVICE PIPING
	211100 - 1



