Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 211119 - FIRE-DEPARTMENT CONNECTIONS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Exposed-type fire-department connections.

2. Flush-type fire-department connections.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each fire-department connection.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 EXPOSED-TYPE FIRE-DEPARTMENT CONNECTION

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Fire Hose & Cabinet.

2. Elkhart Brass Mfg. Company, Inc.

3. Fire-End & Croker Corporation.

4. Fire Protection Products, Inc.

5. GMR International Equipment Corporation.

6. Guardian Fire Equipment, Inc.

7. Venus Fire Protection Ltd.

8. Wilson & Cousins Inc.

9. <Insert manufacturer's name>.

C. Standard: UL 405.

D. Type: Exposed, projecting, for wall mounting.

E. Pressure Rating: 175 psig (1200 kPa) minimum.

F. Body Material: Corrosion-resistant metal.

G. Inlets: Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads. Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

H. Caps: Brass, lugged type, with gasket and chain.

I. Escutcheon Plate: Round, brass, wall type.

J. Outlet: Back, with pipe threads.

K. Number of Inlets: [Two] [Three].

Retain first option in "Escutcheon Plate Marking" Paragraph below if standpipes supply a sprinkler system.

L. Escutcheon Plate Marking: Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

M. Finish: [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

N. Outlet Size: [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)].

2.2 FLUSH-TYPE FIRE-DEPARTMENT CONNECTION

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Fire Hose & Cabinet.

2. Elkhart Brass Mfg. Company, Inc.

3. GMR International Equipment Corporation.

4. Guardian Fire Equipment, Inc.

5. Potter Roemer.

6. Venus Fire Protection Ltd.

7. <Insert manufacturer's name>.

C. Standard: UL 405.

D. Type: Flush, for wall mounting.

E. Pressure Rating: 175 psig (1200 kPa) minimum.

F. Body Material: Corrosion-resistant metal.

G. Inlets: Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads. Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

H. Caps: Brass, lugged type, with gasket and chain.

I. Escutcheon Plate: Rectangular, brass, wall type.

J. Outlet: With pipe threads.

K. Body Style: [Horizontal] [Square] [Vertical].

L. Number of Inlets: [Two] [Three] [Four] [Six].

M. Outlet Location: [Back] [Bottom] [Left side] [Right side] [Top].

Retain first option in "Escutcheon Plate Marking" Paragraph below if standpipes supply a sprinkler system.

N. Escutcheon Plate Marking: Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

O. Finish: [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

P. Outlet Size: [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)] [NPS 8 (DN 200)].

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install wall-type fire-department connections.

B. Install automatic (ball-drip) drain valve at each check valve for fire-department connection.

END OF SECTION 211119

	FIRE-DEPARTMENT CONNECTIONS
	211119 - 1



