Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 211200 - FIRE-SUPPRESSION STANDPIPES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Pipes, fittings, and specialties.

2. Fire-protection specialty valves.

3. Hose connections.

4. Alarm devices.

5. Pressure gages.

B. Related Requirements:

Retain subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 210523 "General-Duty Valves for Water-Based Fire-Suppression Piping."

2. Section 211119 "Fire-Department Connections" for exposed wall-mounted and yard fire hydrants.

3. Section 211213 "Fire-Suppression Hoses and Nozzles" for rack-type hose stations, reel-type hose stations, and monitors.

4. Section 211313 "Wet-Pipe Sprinkler Systems" for wet-pipe sprinkler piping.

5. Section 211316 "Dry-Pipe Sprinkler Systems" for dry-pipe sprinkler piping.

6. [Section 283111 "Digital, Addressable Fire-Alarm System"] [Section 283112 "Zoned (DC Loop) Fire-Alarm System"] for connections to alarm devices.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For fire-suppression standpipes.

1. Include plans, elevations, sections, and attachment details.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

C. Delegated-Design Submittal: For standpipe systems indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1.3 INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For Installer[ and professional engineer].

Retain "Approved Standpipe Drawings" Paragraph below if design by Contractor is specified in "Performance Requirements" Article.

B. Approved Standpipe Drawings: Working plans, prepared according to NFPA 14, that have been approved by authorities having jurisdiction, including hydraulic calculations if applicable.

Retain first paragraph below if report is specified in "Preparation" Article.

C. Fire-hydrant flow test report.

D. Field Test Reports and Certificates: Indicate and interpret test results for compliance with performance requirements and as described in NFPA 14. Include "Contractor's Material and Test Certificate for Aboveground Piping" and "Contractor's Material and Test Certificate for Underground Piping."

E. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below if Contractor is required to assume responsibility for design of fire-suppression standpipes.

A. Installer Qualifications:

Retain subparagraph below if Contractor is required to assume responsibility for engineering.

1. Installer's responsibilities include designing, fabricating, and installing fire-suppression standpipes and providing professional engineering services needed to assume engineering responsibility. Base calculations on results of fire-hydrant flow test.

Retain subparagraph below if Contractor is required to engage a qualified professional engineer.

a. Engineering Responsibility: Preparation of working plans, calculations, and field test reports by a qualified professional engineer.

B. NFPA Standards: Fire-suppression standpipe equipment, specialties, accessories, installation, and testing shall comply with NFPA 14.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 SYSTEM DESCRIPTIONS

A. Automatic Wet-Type, Class II Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations. Has open water-supply valve with pressure maintained and is capable of supplying water demand.

2.2 PERFORMANCE REQUIREMENTS

A. Standard-Pressure, Fire-Suppression Standpipe System Component: Listed for 175-psig (1200-kPa) minimum working pressure.

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

B. Delegated Design: Design fire-suppression standpipes, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain both paragraphs below if system design has not been approved by authorities having jurisdiction.

C. Fire-suppression standpipe design shall be approved by authorities having jurisdiction.

1. Minimum residual pressure at each hose-connection outlet is as follows:

a. NPS 1-1/2 (DN 40) Hose Connections: [65 psig (450 kPa)] <Insert value>.

b. NPS 2-1/2 (DN 65) Hose Connections: [100 psig (690 kPa)] <Insert value>.

D. Seismic Performance: Fire-suppression standpipes shall withstand the effects of earthquake motions determined according to NFPA 13 and [ASCE/SEI 7] <Insert requirement>.

2.3 BLACK STEEL PIPE AND ASSOCIATED FITTINGS

Steel pipes in this article are arranged in order of decreasing wall thickness.

All of the steel piping in this article is suitable for 175-psig (1200-kPa) minimum working pressure.

Retain one of three "Schedule 40" paragraphs below for use with flanged, cut- or roll-grooved, plain-end-pipe, threaded, and welded joints.

A. Schedule 40: ASTM A 53/A 53M, Type E, Grade B; with factory- or field-formed ends to accommodate joining method.

B. Schedule 40: ASTM A 135/A 135M, Grade A; with factory- or field-formed ends to accommodate joining method.

C. Schedule 40: ASTM A 795/A 795M, Type E, Grade A; with factory- or field-formed ends to accommodate joining method.

Retain one of three "Schedule 30" paragraphs below for use with flanged, roll-grooved, plain-end-pipe, threaded, and welded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250).

D. Schedule 30: ASTM A 53/A 53M, Type E, Grade B; with factory- or field-formed ends to accommodate joining method.

E. Schedule 30: ASTM A 135/A 135M, Grade A; with factory- or field-formed ends to accommodate joining method.

F. Schedule 30: ASTM A 795/A 795M, Type E, Grade A; with factory- or field-formed ends to accommodate joining method.

Retain one of three "Thinwall" paragraphs below for use with flanged, roll-grooved, plain-end-pipe, threaded, and welded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250).

G. Thinwall: ASTM A 53/A 53M, Type E; with wall thickness less than Schedule 30 and equal to or greater than Schedule 10; and with factory- or field-formed ends to accommodate joining method.

H. Thinwall: ASTM A 135/A 135M, Grade A; with wall thickness less than Schedule 30 and equal to or greater than Schedule 10; and with factory- or field-formed ends to accommodate joining method.

I. Thinwall: ASTM A 795/A 795M, Type E, Grade A; with wall thickness less than Schedule 30 and equal to or greater than Schedule 10; and with factory- or field-formed ends to accommodate joining method.

Couplings in "Uncoated, Steel Couplings" Paragraph below are available in NPS 1/8 to NPS 20 (DN 6 to DN 500).

J. Uncoated, Steel Couplings: ASTM A 865/A 865M, threaded.

Fittings in "Uncoated, Gray-Iron Threaded Fittings" Paragraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

K. Uncoated, Gray-Iron Threaded Fittings: ASME B16.4, Class 125, standard pattern.

Unions in "Malleable- or Ductile-Iron Unions" Paragraph below are available in NPS 1/4 to NPS 3 (DN 8 to DN 80), but NPFA limits them to NPS 2 (DN 50) and smaller.

L. Malleable- or Ductile-Iron Unions: UL 860.

Flanges in "Cast-Iron Flanges" Paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

M. Cast-Iron Flanges: ASME B16.1, Class 125.

Flanges and fittings in "Steel Flanges and Flanged Fittings" Paragraph below are available in NPS 1/2 to NPS 24 (DN 15 to DN 600).

N. Steel Flanges and Flanged Fittings: ASME B16.5, Class 150.

Fittings in "Steel Welding Fittings" Paragraph below are available in NPS 1/2 to NPS 48 (DN 15 to DN 1200).

O. Steel Welding Fittings: ASTM A 234/A 234M and ASME B16.9.

P. Grooved-Joint, Steel-Pipe Appurtenances:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Corcoran Piping System Co.

c. National Fittings, Inc.

d. Shurjoint Piping Products.

e. Tyco Fire & Building Products LP.

f. Victaulic Company.

g. <Insert manufacturer's name>.

2. Pressure Rating: [175 psig (1200 kPa)] [250 psig (1725 kPa)] [300 psig (2070 kPa)] minimum.

3. [Galvanized] [and] [Uncoated], Grooved-End Fittings for Steel Piping: ASTM A 47/A 47M, malleable-iron casting or ASTM A 536, ductile-iron casting; with dimensions matching steel pipe.

AWWA C606 and UL 213 cover couplings in "Grooved-End-Pipe Couplings for Steel Piping" Subparagraph below in NPS 3/4 to at least NPS 12 (DN 20 to at least DN 300).

4. Grooved-End-Pipe Couplings for Steel Piping: AWWA C606 and UL 213, rigid pattern, unless otherwise indicated, for steel-pipe dimensions. Include ferrous housing sections, EPDM-rubber gasket, and bolts and nuts.

2.4 GALVANIZED-STEEL PIPE AND ASSOCIATED FITTINGS

Steel pipes in this article are arranged in order of decreasing wall thickness.

All of the steel piping in this article is suitable for 175-psig (1200-kPa) minimum working pressure.

Retain one of three "Schedule 40" paragraphs below for use with flanged, cut- or roll-grooved, plain-end-pipe, threaded, and welded joints. Pipe is available in NPS 1/8 to NPS 26 (DN 6 to DN 650).

A. Schedule 40: ASTM A 53/A 53M, Type E, Grade B; with factory- or field-formed ends to accommodate joining method.

B. Schedule 40: ASTM A 135/A 135M, Grade A; with factory- or field-formed ends to accommodate joining method.

C. Schedule 40: ASTM A 795/A 795M, Type E, Grade A; with factory- or field-formed ends to accommodate joining method.

Nipples in "Galvanized-Steel Pipe Nipples" Paragraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

D. Galvanized-Steel Pipe Nipples: ASTM A 733, made of ASTM A 53/A 53M or ASTM A 106/A 106M, Standard Weight, seamless steel pipe with threaded ends.

Fittings in "Galvanized, Gray-Iron Threaded Fittings" Paragraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

E. Galvanized, Gray-Iron Threaded Fittings: ASME B16.4, Class 125, standard pattern.

Unions in "Malleable-Iron Unions" Paragraph below are available in NPS 1/8 to NPS 4 (DN 6 to DN 100).

F. Malleable-Iron Unions:

1. ASME B16.39, Class 150.

2. Hexagonal-stock body.

3. Ball-and-socket, metal-to-metal, bronze seating surface.

4. Threaded ends.

Flanges in "Flanges" Paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

G. Flanges: ASME B16.1, Class 125, cast iron.

H. Appurtenances for Grooved-End, Galvanized-Steel Pipe:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Anvil International, Inc.

b. Grinnell Mechanical Products; Tyco Fire Products LP.

c. Shurjoint Piping Products.

d. Victaulic Company.

e. <Insert manufacturer's name>.

3. Fittings for Grooved-End, Galvanized-Steel Pipe: Galvanized, ASTM A 47/A 47M, malleable-iron casting; ASTM A 106/A 106M, steel pipe; or ASTM A 536, ductile-iron casting; with dimensions matching steel pipe.

In "Fittings for Grooved-End, Galvanized-Steel Pipe" Subparagraph below, AWWA C606 covers couplings in NPS 3/4 to NPS 24 (DN 20 to DN 600).

4. Fittings for Grooved-End, Galvanized-Steel Pipe:

a. AWWA C606 for steel-pipe dimensions.

b. Ferrous housing sections.

c. EPDM-rubber gaskets suitable for hot and cold water.

d. Bolts and nuts.

e. Minimum Pressure Rating:

1) NPS 8 (DN 200) and Smaller: [600 psig (4137 kPa)] <Insert value>.

2) NPS 10 and NPS 12 (DN 250 to DN 300): [400 psig (2758 kPa)] <Insert value>.

3) NPS 14 to NPS 24 (DN 350 to DN 600): [250 psig (1725 kPa)] <Insert value>.

2.5 PIPING JOINING MATERIALS

A. Pipe-Flange Gasket Materials: [AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick] [or] [ASME B16.21, nonmetallic and asbestos free].

1. Class 125, Cast-Iron Flanges and Class 150, Bronze Flat-Face Flanges: Full-face gaskets.

2. Class 250, Cast-Iron Flanges and Class 300, Steel Raised-Face Flanges: Ring-type gaskets.

B. Metal, Pipe-Flange Bolts and Nuts: ASME B18.2.1, carbon steel unless otherwise indicated.

C. Welding Filler Metals: Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

2.6 SPECIALTY VALVES

A. General Requirements:

1. Standard: UL's "Fire Protection Equipment Directory" listing or FM Global's "Approval Guide."

2. Pressure Rating: 175 psig (1200 kPa) minimum.

3. Body Material: Cast or ductile iron.

4. Size: Same as connected piping.

5. End Connections: Flanged or grooved.

Valves in "Alarm Valves" Paragraph below are available in NPS 1-1/2 to NPS 8 (DN 40 to DN 200).

B. Alarm Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Globe Fire Sprinkler Corporation.

b. Reliable Automatic Sprinkler Co., Inc.

c. Tyco Fire & Building Products LP.

d. Venus Fire Protection Ltd.

e. Victaulic Company.

f. Viking Corporation.

g. <Insert manufacturer's name>.

3. Standard: UL 193.

4. Design: For horizontal or vertical installation.

Delete option in first subparagraph below if water-supply pressure is constant.

5. Include trim sets for bypass, drain, electrical sprinkler alarm switch, pressure gages,[ retarding chamber,] and fill-line attachment with strainer.

Retain one of two "Drip Cup Assembly" subparagraphs below. Retain first subparagraph if retarding chamber is required. Retain second if retarding chamber is not required.

6. Drip Cup Assembly: Pipe drain without valves and separate from main drain piping.

7. Drip Cup Assembly: Pipe drain with check valve to main drain piping.

Valves in "Pressure-Reducing Valves" Paragraph below are used on standpipe risers.

C. Pressure-Reducing Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. CLA-VAL Automatic Control Valves.

b. Fire-End & Croker Corporation.

c. Fire Protection Products, Inc.

d. Guardian Fire Equipment, Inc.

e. OCV Control Valves.

f. Potter Roemer.

g. Zurn Plumbing Products Group; Wilkins Water Control Products Division.

h. <Insert manufacturer's name>.

Indicate valve size and inlet and outlet pressures on Drawings for each pressure-reducing valve.

3. UL 668 hose valve, with integral UL 1468 reducing device.

4. Pressure Rating: 300 psig (2070 kPa) minimum.

5. Material: Brass or bronze.

6. Inlet: Female pipe threads.

7. Outlet: Threaded with or without adapter having male hose threads.

8. Pattern: [Angle] [or] [gate].

9. Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

D. Automatic (Ball Drip) Drain Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Reliable Automatic Sprinkler Co., Inc.

b. Tyco Fire & Building Products LP.

c. <Insert manufacturer's name>.

3. Standard: UL 1726.

4. Pressure Rating: 175 psig (1200 kPa) minimum.

5. Type: Automatic draining, ball check.

6. Size: NPS 3/4 (DN 20).

7. End Connections: Threaded.

2.7 HOSE CONNECTIONS

Coordinate cabinets with Section 104413 "Fire Protection Cabinets." Indicate size and design outlet pressure setting on Drawings for each hose connection.

A. Nonadjustable-Valve Hose Connections:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Brooks Equipment Co., Inc.

b. Elkhart Brass Mfg. Company, Inc.

c. Fire-End & Croker Corporation.

d. Fire Protection Products, Inc.

e. GMR International Equipment Corporation.

f. Guardian Fire Equipment, Inc.

g. Kennedy Valve; a division of McWane, Inc.

h. Mueller Co.; Water Products Division.

i. NIBCO INC.

j. Potter Roemer.

k. Tyco Fire & Building Products LP.

l. Viking Corporation.

m. Wilson & Cousins Inc.

n. <Insert manufacturer's name>.

3. Standard: UL 668 hose valve for connecting fire hose.

4. Pressure Rating: 300 psig (2070 kPa) minimum.

5. Material: Brass or bronze.

6. Size: NPS 1-1/2 (DN 40), as indicated.

7. Inlet: Female pipe threads.

8. Outlet: Male hose threads with lugged cap, gasket, and chain. Include hose valve threads according to NFPA 1963 and matching local fire-department threads.

9. Pattern: [Angle] [or] [gate].

10. Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

2.8 ALARM DEVICES

A. Alarm-device types shall match piping and equipment connections.

Retain remaining paragraphs if devices are specified in this Section, or delete if devices are specified in Section 283111 "Digital, Addressable Fire-Alarm System" and Section 283112 "Zoned (DC Loop) Fire-Alarm System."

B. Water-Motor-Operated Alarm:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Globe Fire Sprinkler Corporation.

b. Tyco Fire & Building Products LP.

c. Victaulic Company.

d. Viking Corporation.

e. <Insert manufacturer's name>.

2. Standard: UL 753.

3. Type: Mechanically operated, with pelton wheel.

4. Alarm Gong: Cast aluminum with red-enamel factory finish.

5. Size: 10-inch (250-mm) diameter.

6. Components: Shaft length, bearings, and sleeve to suit wall construction.

7. Inlet: NPS 3/4 (DN 20).

8. Outlet: NPS 1 (DN 25) drain connection.

C. Electrically Operated Alarm Bell:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fire-Lite Alarms, Inc.; a Honeywell company.

b. Notifier; a Honeywell company.

c. Potter Electric Signal Company.

d. <Insert manufacturer's name>.

2. Standard: UL 464.

3. Type: Vibrating, metal alarm bell.

4. Size: [6-inch (150-mm) minimum] [8-inch (200-mm) minimum] [10-inch (250-mm)] diameter.

5. Finish: Red-enamel factory finish, suitable for outdoor use.

D. Water-Flow Indicators:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ADT Security Services, Inc.

b. McDonnell & Miller; ITT Industries.

c. Potter Electric Signal Company.

d. System Sensor; a Honeywell company.

e. Viking Corporation.

f. Watts Industries (Canada) Inc.

g. <Insert manufacturer's name>.

2. Standard: UL 346.

3. Water-Flow Detector: Electrically supervised.

4. Components: Two single-pole, double-throw circuit switches for isolated alarm and auxiliary contacts, 7 A, 125-V ac and 0.25 A, 24-V dc; complete with factory-set, field-adjustable retard element to prevent false signals and tamperproof cover that sends signal if removed.

5. Type: Paddle operated.

6. Pressure Rating: 250 psig (1725 kPa).

7. Design Installation: Horizontal or vertical.

E. Pressure Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Barksdale, Inc.

b. Detroit Switch, Inc.

c. Potter Electric Signal Company.

d. System Sensor; a Honeywell company.

e. Tyco Fire & Building Products LP.

f. United Electric Controls Co.

g. Viking Corporation.

h. <Insert manufacturer's name>.

2. Standard: UL 346.

3. Type: Electrically supervised water-flow switch with retard feature.

4. Components: Single-pole, double-throw switch with normally closed contacts.

5. Design Operation: Rising pressure signals water flow.

F. Valve Supervisory Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Fire-Lite Alarms, Inc.; a Honeywell company.

b. Kennedy Valve; a division of McWane, Inc.

c. Potter Electric Signal Company.

d. System Sensor; a Honeywell company.

e. <Insert manufacturer's name>.

2. Standard: UL 346.

3. Type: Electrically supervised.

4. Components: Single-pole, double-throw switch with normally closed contacts.

5. Design: Signals that controlled valve is in other than fully open position.

G. Indicator-Post Supervisory Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Potter Electric Signal Company.

b. System Sensor; a Honeywell company.

c. <Insert manufacturer's name>.

2. Standard: UL 346.

3. Type: Electrically supervised.

4. Components: Single-pole, double-throw switch with normally closed contacts.

5. Design: Signals that controlled indicator-post valve is in other than fully open position.

2.9 PRESSURE GAGES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. AMETEK; U.S. Gauge Division.

2. Ashcroft Inc.

3. Brecco Corporation.

4. WIKA Instrument Corporation.

5. <Insert manufacturer's name>.

B. Standard: UL 393.

C. Dial Size: 3-1/2- to 4-1/2-inch (90- to 115-mm) diameter.

D. Pressure Gage Range: [Zero to 250 psig (Zero to 1725 kPa) minimum] [Zero to 300 psig (Zero to 2070 kPa)].

E. Water System Piping Gage: Include "WATER" or "AIR/WATER" label on dial face.

F. Air System Piping Gage: Include[ retard feature and] "AIR" or "AIR/WATER" label on dial face.

PART 3 -  EXECUTION

3.1 PREPARATION

Retain this article if fire-hydrant flow test is required or if Owner has not provided flow information.

A. Perform fire-hydrant flow test according to NFPA 14 and NFPA 291. Use results for system design calculations required in "Quality Assurance" Article.

B. Report test results promptly and in writing.

3.2 SERVICE-ENTRANCE PIPING

Retain this article and delete "Water-Supply Connections" Article if connection to building's water-service piping is required.

A. Connect fire-suppression standpipe piping to water-service piping at service entrance into building. Comply with requirements for exterior piping in Section 211100 "Facility Fire-Suppression Water-Service Piping."

Retain one of two paragraphs below. Backflow preventers are recommended and are usually required by authorities having jurisdiction. Do not specify backflow preventers here if they are specified in Section 211100 "Facility Fire-Suppression Water-Service Piping."

B. Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories at connection to fire-suppression water-service piping.[ Comply with requirements for backflow preventers in Section 211100 "Facility Fire-Suppression Water-Service Piping."]

C. Install shutoff valve, check valve, pressure gage, and drain at connection to water service.

3.3 WATER-SUPPLY CONNECTIONS

Retain this article and delete "Service-Entrance Piping" Article if connection to building's water-distribution piping is required.

A. Connect fire-suppression standpipe piping to building's interior water-distribution piping. Comply with requirements for interior piping in Section 221116 "Domestic Water Piping."

Retain one of two paragraphs below. Backflow preventers are recommended and are usually required by authorities having jurisdiction.

B. Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories at connection to water-distribution piping.[ Comply with requirements for backflow preventers in Section 221119 "Domestic Water Piping Specialties."]

C. Install shutoff valve, check valve, pressure gage, and drain at connection to water supply.

3.4 PIPING INSTALLATION

A. Locations and Arrangements: Drawing plans, schematics, and diagrams indicate general location and arrangement of piping. Install piping as indicated, as far as practical.

1. Deviations from approved working plans for piping require written approval from authorities having jurisdiction. File written approval with Architect before deviating from approved working plans.

B. Piping Standard: Comply with requirements in NFPA 14 for installation of fire-suppression standpipe piping.

Retain first paragraph below if piping is required to withstand seismic design loads.

C. Install seismic restraints on piping. Comply with requirements in NFPA 13 for seismic-restraint device materials and installation.

D. Install listed fittings to make changes in direction, branch takeoffs from mains, and reductions in pipe sizes.

E. Install drain valves on standpipes. Extend drain piping to outside of building.

F. Install automatic (ball drip) drain valves to drain piping between fire-department connections and check valves. Drain to floor drain or outside building.

G. Install alarm devices in piping systems.

See Editing Instruction No. 3 in the Evaluations for cautions about pipe hangers.

H. Install hangers and supports for standpipe system piping according to NFPA 14. Comply with requirements in NFPA 13 for hanger materials.

I. Install pressure gages on riser or feed main and at top of each standpipe. Include pressure gages with connection not less than NPS 1/4 (DN 8) and with soft-metal seated globe valve, arranged for draining pipe between gage and valve. Install gages to permit removal, and install where they are not subject to freezing.

J. Fill standpipe system piping with water.

K. Install electric heating cables and pipe insulation on wet-type fire-suppression standpipe piping in areas subject to freezing. Comply with requirements for heating cables in Section 210533 "Heat Tracing for Fire-Suppression Piping" and for piping insulation in Section 210700 "Fire-Suppression Systems Insulation."

L. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

M. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

N. Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 210518 "Escutcheons for Fire-Suppression Piping."

3.5 JOINT CONSTRUCTION

A. Install couplings, flanges, flanged fittings, unions, nipples, and transition and special fittings that have finish and pressure ratings same as or higher than system's pressure rating for aboveground applications unless otherwise indicated.

B. Install unions adjacent to each valve in pipes NPS 2 (DN 50) and smaller.

C. Install flanges, flange adapters, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

D. Ream ends of pipes and tubes, and remove burrs. Bevel plain ends of steel pipe.

E. Remove scale, slag, dirt, and debris from inside and outside of pipes, tubes, and fittings before assembly.

F. Flanged Joints: Select appropriate gasket material in size, type, and thickness suitable for water service. Join flanges with gasket and bolts according to ASME B31.9.

G. Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads.

2. Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged.

H. Steel-Piping, Cut-Grooved Joints: Cut square-edge groove in end of pipe according to AWWA C606. Assemble coupling with housing, gasket, lubricant, and bolts. Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe joints.

I. Steel-Piping, Roll-Grooved Joints: Roll rounded-edge groove in end of pipe according to AWWA C606. Assemble coupling with housing, gasket, lubricant, and bolts. Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe grooved joints.

J. Welded Joints: Construct joints according to AWS D10.12/D10.12M, using qualified processes and welding operators according to "Quality Assurance" Article.

1. Shop weld pipe joints where welded piping is indicated. Do not use welded joints for galvanized-steel pipe.

3.6 VALVE AND SPECIALTIES INSTALLATION

A. Install listed fire-protection valves, trim and drain valves, specialty valves and trim, controls, and specialties according to NFPA 14 and authorities having jurisdiction.

B. Install listed fire-protection shutoff valves supervised-open, located to control sources of water supply except from fire-department connections. Install permanent identification signs indicating portion of system controlled by each valve.

C. Install check valve in each water-supply connection. Install backflow preventers instead of check valves in potable-water-supply sources.

D. Specialty Valves:

1. General Requirements: Install in vertical position for proper direction of flow, in main supply to system.

2. Alarm Valves: Install bypass check valve and retarding chamber drain-line connection.

3.7 HOSE-CONNECTION INSTALLATION

Indicate hose-connection locations, sizes, and special devices on Drawings.

A. Install hose connections adjacent to standpipes.

B. Install freestanding hose connections for access and minimum passage restriction.

C. Install NPS 1-1/2 (DN 40) hose-connection valves with flow-restricting device.

D. Install wall-mounted-type hose connections in cabinets. Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet. Install valves at angle required for connection of fire hose. Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

3.8 HOSE-STATION INSTALLATION

Indicate hose-station locations, sizes, and special devices on Drawings.

A. Install freestanding hose stations for access and minimum passage restriction.

B. Install NPS 1-1/2 (DN 40) hose-station valves with flow-restricting device unless otherwise indicated.

C. Install freestanding hose stations with support or bracket attached to standpipe.

D. Install wall-mounted, rack hose stations in cabinets. Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet. Install valves at angle required for connection of fire hose. Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

E. Install hose-reel hose stations on wall with bracket.

3.9 FIRE-DEPARTMENT CONNECTION INSTALLATION

A. Install wall-type fire-department connections.

B. Install yard-type fire-department connections in concrete slab support. Comply with requirements for concrete in Section 033000 "Cast-in-Place Concrete."

1. Install [two] [three] <Insert number> protective pipe bollards [around] [on sides of] each fire-department connection. Comply with requirements for bollards in Section 055000 "Metal Fabrications."

C. Install automatic (ball drip) drain valve at each check valve for fire-department connection.

3.10 IDENTIFICATION

A. Install labeling and pipe markers on equipment and piping according to requirements in NFPA 14.

B. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

3.11 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Leak Test: After installation, charge systems and test for leaks. Repair leaks and retest until no leaks exist.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

3. Flush, test, and inspect standpipe systems according to NFPA 14, "System Acceptance" Chapter.

4. Energize circuits to electrical equipment and devices.

5. Start and run air compressors.

6. Coordinate with fire-alarm tests. Operate as required.

7. Coordinate with fire-pump tests. Operate as required.

8. Verify that equipment hose threads are same as local fire-department equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Fire-suppression standpipe system will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

3.12 DEMONSTRATION

A. Train Owner's maintenance personnel to adjust, operate, and maintain specialty valves.

3.13 PIPING SCHEDULE

See Editing Instruction No. 2 in the Evaluations for available materials.

Retain piping applications in this article. Coordinate with materials specified in Part 2.

A. Piping between Fire-Department Connections and Check Valves: Galvanized, Schedule 40, steel pipe with [threaded ends; cast-iron threaded fittings; and threaded] [grooved ends; grooved-end fittings; grooved-end-pipe couplings; and grooved] joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Wet-type fire-suppression standpipe piping, [NPS 4 (DN 100) and smaller] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of five subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Schedule 40] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

2. [Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

3. [Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

4. Thinwall black-steel pipe with roll-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

5. Thinwall black-steel pipe with plain ends; welding fittings; and welded joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

C. Standard-pressure, wet-type fire-suppression standpipe piping, [NPS 5 to NPS 8 (DN 125 to DN 200)] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of five subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Schedule 40] [Schedule 30] [or] [thinwall], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

2. [Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

3. [Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

4. Thinwall black-steel pipe with roll-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

5. Thinwall black-steel pipe with plain ends; welding fittings; and welded joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

D. Standard-pressure, wet-type fire-suppression standpipe piping, [NPS 10 and NPS 12 (DN 250 and DN 300)] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of four subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

1. [Schedule 40] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

2. [Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

3. [Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

4. Thinwall black-steel pipe with plain ends; welding fittings; and welded joints.

END OF SECTION 211200

	FIRE-SUPPRESSION STANDPIPES
	211200 - 1



